NATIONAL IDENTIFICATION AUTHORITY

(NIA)

TENDER DOCUMENTS

PROCUREMENT OF GOODS

PRICE QUOTATION

SUPPLY AND INSTALLATION OF REMOTE MONITORING SYSTEM FOR NIA GENERATOR SETS

RFQ No. GR/NIA/0021/2026

# Table of Contents

Table of Contents	2

Section I. Invitation for Price Quotation	3

Section II. Conditions of Contract	6

Section III. Form of Contract	10

Section IV. Sample Forms	11

Price Schedule	12

Section V. Schedule of Requirements	13

TECHNICAL SPECIFICATIONS	14

# Section I. Invitation for Price Quotation

Name of Procurement Entity: 	     NATIONAL IDENTIFICATION AUTHORITY

Address of Procurement Entity:              No.8, Nelson Mandela Avenue, Off Gulf House 					                  Street, South Legon, Accra

P.O. Box M-680, Ministries – Accra

RFQ No:                                                  (GR/NIA/GD/0021/2026)

Date of Invitation:                                    19/06/2026

- The National Identification Authority intends to use part of its budgetary allocation to make eligible payment under the contract for Supply and Installation of Remote Monitoring System for NIA Generators Sets for which this invitation for Quotations is issued.

- The National Identification Authority now invites Quotations from eligible registered suppliers for the supply of items listed in the table below and specified in the Section V, Schedule of Requirements;

| S/N | DESCRIPTION | QTY |
| --- | --- | --- |
|  | Remote Monitoring System for 1No 500KVA and 2No 350KVA Generator Sets | 1 |

- The deadline for submission of Quotation is 26th June 2026 at 10:00 AM. Quotations must be submitted electronically via http://www.ghaneps.gov.gh, For the purpose of clarification, kindly Contact the Employer on the address given below:

PROCUREMENT UNIT

FIRST FLOOR

NATIONAL IDENTIFICATION AUTHORITY

HEAD OFFICE, SOUTH LEGON, ACCRA

Digital Address: GA-237-1033

procurement@nia.gov.gh

- The sealed Quotations shall remain valid for 90 days from the date of submission.

- Your Quotes shall include all taxes and delivery to the Stores, National Identification Authority pursuant to clause 16 of the Conditions of Contract.

- The prices quoted shall be Delivery Duty Paid (DDP) to Stores, National Identification Authority, Accra, Ghana.

- Prices shall be quoted in Ghana cedis and shall remain fixed over the period of the contract.

- Delivery schedule: Delivery SHALL NOT exceed 30 days after award of Contract. When delivery is not made by the said delivery period, the contract may be deemed cancelled.

- Your Quotes will be evaluated on the basis of specification, Price, Delivery and Payment Terms in addition to the evaluation criteria specified in clause 10 below.

- It is mandatory that Tenderers include in their Quotation the under listed statutory requirement.

- Duly completed and signed Tender Form and Price Schedule furnished in Section IV of this Request for Quotations Document

- Valid Business Registration Documents

- Valid Tax Clearance Certificate

- Valid SSNIT Clearance Certificate

- Valid VAT Registration Certificate

- Valid Public Procurement Authority Certificate

- Sample/Brochure

- Warranty

- Quotations without the above stated requirement would be considered incomplete and shall be disqualified.

Thanks for your co-operation

Signed

MR. ISAAC TETTEH

HEAD, PROCUREMENT

# Section II. Conditions of Contract

| 1. Definitions | 1.1 | In this contract, the following terms shall be interpreted as indicated: a. "The Contract" means the agreement entered into between the Purchaser and the Supplier, as recorded in the Contract Form Signed by the parties, including all attachments and appendices thereto and all documents incorporated by reference therein; b. "The Contract Price" means the price payable to the Supplier under the contract for the full and proper performance of its contractual obligation; c. "The Goods" means Equipment and related Accessories and spare-parts which the Supplier is required to supply to the Purchaser under the contract; d. "Services" means services ancillary to the supply of the goods such as transportation and insurance including the installation, commissioning and the operational and maintenance training of the supplied equipment. e. "The Purchaser" means the organization purchasing the goods; f. "The Supplier" means the organization supplying the goods and services under this contract. |
| --- | --- | --- |
| 2. Technical Specification | 2.1 | The goods supplied under this contract shall conform to the standards mentioned in the Technical Specification. |
| 3. Patent Right | 3.1 | The Supplier shall indemnify the Purchaser against all third party claims of infringement of patent, trademark or industrial design rights arising from use of goods or any part thereof in the Purchaser's country. |
| 4. Inspection and Tests | 4.1 | The Purchaser or its Representative shall have the right to inspect and/or test the goods to confirm their conformity to the Technical Specification and the quality of performance after the supply and delivery of good to Purchaser's premises. |
| 5. Packing | 5.1 | The Supplier shall provide such packing of the goods as is required to prevent their damage or deterioration during transit to their final destination as indicated in the contract. |
|  | 5.2 | The packing shall be sufficient to withstand, without limitation, rough handling during transit and exposure to extreme temperatures, salt and precipitation during transit and open storage. |
|  | 5.3 | Packing case, size and weights shall take into consideration, where appropriate, the remoteness of the goods' final destination and the absence of heavy handling facilities at all points in transit. |
|  | 5.4 | The packing, marking and documentation within and outside the packages shall comply strictly with such special requirements as shall be expressly provided in accordance with international standard and practice. |
| 6. Delivery of Goods | 6.1 | Delivery of the goods shall be made by the Supplier in accordance with the terms specified by the Purchaser in its schedule of requirements. |
|  | 6.2 | For purposes of the contract "FOB", "C&F", "CIF", "CIP" and other trade terms used to describe the obligations of the parties shall have the meanings assigned to them by the current edition of the International Rules for the Interpretation of the Trade Terms (INCOTERMS) published by the International Chamber of Commerce (ICC), Paris. |
| 7. Insurance | 7.1 | The goods supplied under the contract shall be fully insured in the currency of the bid price against loss or damage incidental to manufacture or acquisition, transportation, storage and delivery in the manner specified. |
|  | 7.2 | Where delivery of the goods is required by the Purchaser on a CIF or CIP basis to a specified destination, the Supplier shall arrange and pay for insurance, naming the Purchaser as the Beneficiary and the Supplier shall be required to meet all transport and storage expenses until delivery. |
| 8. Warranty | 8.1 | The Supplier warrants that all the goods supplied under the contract shall fully comply with the specification laid down in the contract. |
|  | 8.2 | The warranty shall remain valid for one year after the goods have been delivered to the final destination indicated in the contract, and accepted by the Purchaser after installation and commissioning of equipment by the Supplier. |
|  | 8.3 | The Purchaser shall promptly notify the Supplier in writing of any claims arising under this warranty. |
|  | 8.4 | Upon receipt of such notice, the Supplier shall, within 30 days replace the defective goods without cost to the Purchaser. The Supplier will be required to remove, at its own risk and cost, the defective goods. |
| 9. Payment | 9.1 | Payment shall be made in the currency in which the contract price has been stated in the Supplier's Sealed Quotation |
|  | 9.2 | Payment of the goods supplied from within Ghana shall be made in Ghanaian Cedis within 60 Days after the delivery and installation and commissioning of goods to the satisfaction of the Purchaser. |
|  | 9.3 | Payment of the goods to be supplied from abroad shall be made in the following manner: NOT APPLICABLE a. On shipment: Eighty (80) percent of the contract price of the Goods shipped shall be paid through irrevocable confirmed letter of credit opened in favour of the Supplier in a bank in its country, upon submission of documents. - On acceptance: Twenty (20) percent of the contract price of goods received shall be paid within thirty (30) days of receipt of the goods upon submission of claim supported by the acceptance certificate issued by the Purchaser. Or - Full payment on satisfactory delivery and acceptance of goods. |
| 10. Prices | 10.1 | Prices charged by the Supplier for goods delivered under the contract shall not vary from the prices quoted by the Supplier in its sealed quotation. |
| 11. Liquidated Damages | 11.1 | If the Supplier fails to deliver any or all of the goods within the time period specified in the contract, the Purchaser shall, without prejudice to its other remedies under the contract, deduct from the contract price, as liquidated damages, a sum equivalent to 1.0 percent of the contract price of delayed goods for each week of delay until actual delivery, up to a maximum deduction of 10 percent of the delayed goods' contract price. Once the maximum is reached, the Purchaser may consider termination of the contract. |
| 12. Resolution of Disputes | 12.1 | The Purchaser and Supplier shall make every effort to resolve amicably by direct informal negotiation any disagreement or dispute arising between them under or in connection with the contract. |
|  | 12.2 | If, after thirty (30) days from the commencement of such informal negotiation, the Purchaser and Supplier have been unable to resolve amicably a contract dispute, it shall be referred by either party to an adjudicator agreed by the parties. In the event of disagreement the adjudicator shall be appointed in accordance with the Laws and Rules of Ghana. |
| 13. Governing Language | 13.1 | The Governing Language shall be English |
| 14. Applicable Law | 14.1 | The applicable law shall be the Laws of Ghana. |
| 15. Notices | 15.1 | Purchaser's address for notice purposes: NATIONAL IDENTIFICATION AUTHORITY No.8, Nelson Mandela Avenue, Off Gulf House Street, South Legon, Accra P.O. Box M-680, Ministries – Accra |
|  | 15.2 | Supplier’s address for notice purposes: |
| 16. Taxes and Duties | 16.1 | The Supplier shall be entirely responsible for all taxes, duties, License fees and other such levies imposed by the Government of Ghana. |
| 17. Operation, Maintenance and Spare-parts Manuals | 17.1 | The successful Supplier shall supply 2 copies of manufacturer's operation, maintenance and spare-part manuals of the goods (Equipment). |

# Section III. Form of Contract

THIS AGREEMENT made the _____ day of __________ 20_____ between [name of

Purchaser] (hereinafter called “the Purchaser”) of the one part and [name of Supplier] of [city and country of Supplier] (hereinafter called “the Supplier”) of the other part:

WHEREAS the Purchaser invited bids for certain goods and ancillary services, viz.,

________________________________________________________________________________________________________________________________________________

[brief description of goods and services]

and has accepted a tender by the Supplier for the supply of those goods and services in the sum of [contract price in words and figures] (hereinafter called “the Contract Price”).

NOW THIS AGREEMENT WITNESSETH AS FOLLOWS:

1. In this Agreement words and expressions shall have the same meanings as are

respectively assigned to them in the Conditions of Contract referred to.

2. The following documents shall be deemed to form and be read and construed as part of

this Agreement, viz.:

a. Tender Form and the Price Schedule submitted by the Supplier;

b. The Schedule of Requirements;

c. The Technical Specifications;

d. The Conditions of Contract; and

e. The Purchaser’s Notification of Award.

3. In consideration of the payments to be made by the Purchaser to the Supplier as

Hereinafter mentioned, the Supplier hereby covenants with the Purchaser to provide the

Goods and services and to remedy defects therein in conformity in all respects with the

Provisions of the Contract.

4. The Purchaser hereby covenants to pay the Supplier in consideration of the provision of the goods and services and the remedying of defects therein, the Contract Price or such

other sum as may become payable under the provisions of the contract at the times and

in the manner prescribed by the Contract.

IN WITNESS whereof the parties hereto have caused this Agreement to be executed in

Accordance with their respective laws the day and year first above written.

| On behalf of the Purchaser | On behalf of the Supplier |
| --- | --- |
| Name: | Name: |
| Designation: | Designation: |
| Sign: | Sign: |
| Seal: | Seal: |

# Section IV. Sample Forms

1. Tender and Price Schedules

Date:

To: [name and address of Purchaser]

Gentlemen and/or Ladies:

Having examined the tender documents, we the undersigned, offer to supply and deliver

________________________________________________________________________________________________________________________________________________

[description of goods and services]

in conformity with the said tender documents for the sum of _________________, ______________  [total tender amount in words and figures] or such other sums as may be ascertained in accordance with the Schedule of Prices attached herewith and made part of this Tender.

We undertake, if our Tender is accepted, to deliver the goods in accordance with the delivery schedule specified in the Schedule of Requirements.

If our Tender is accepted, we will obtain the guarantee of a bank in a sum equivalent to _____ percent of the Contract Price for the due performance of the Contract, in the form prescribed by the Purchaser.

We agree to abide by this Tender for a Period of _____ [number] days from the date fixed for Tender opening it shall remain binding upon us and may be accepted at any time before the expiration of that period.

Until a formal Contract is prepared and executed, this Tender, together with your written acceptance thereof and your notification of award, shall constitute a binding Contract between us.

We understand that you are not bound to accept the lowest or any tender you may receive.

Dated this ______________________ day of ________________ 20______.

_______________________			______________________________

[signature]						 [in the capacity of]

Duly authorized to sign Tender for and on behalf of _________________________

# Price Schedule

Name of Supplier ____________________________ Page _________ of __________

| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Unit | Product Description | Country of Origin | Qty Offered | Unit Price | Cost of incidental services | VAT and other Taxes payable if Contract is Awarded | Total DDP Price per item 9=([5x6] 7+8) |

| Total Price to final destination…………………………………………………………… |  |
| --- | --- |

Signature of Tenderer

Note: In case of discrepancy between unit price and total, the unit price shall prevail.

# Section V. Schedule of Requirements

The delivery schedule expressed as weeks/months stipulates hereafter a delivery date which is the date of delivery (i) at EXW premises, or (ii) to the carrier at the port of shipment when the contract is placed on FOB or CIF terms, or (iii) to the first carrier when the contract is placed on FCA or CIP terms. In order to determine the correct date of delivery hereafter specified, the Purchaser has taken into account the additional time that will be needed for international or national transit to the Project Site or to another common place.

| S/N | Unit Size | Description | Qty. | Delivery Schedule |
| --- | --- | --- | --- | --- |
|  | 1 | Remote Monitoring System for 1 No 500KVA and 2 No 350KVA Generator Sets | 1 | Within 30 days after award of Contract |

# TECHNICAL SPECIFICATIONS

| S/N | Minimum required specifications: | Offered specifications |
| --- | --- | --- |
|  | General Requirements The proposed solution shall provide a cloud-based Remote Monitoring System (RMS) for standby diesel generators, enabling real-time monitoring, alarm management, analytics and operational reporting. The system shall support deployment across multiple sites and provide a single centralised dashboard accessible through a secure web interface. The solution shall be modular, scalable, and suitable for operation in mission-critical facilities, including data centres and government institutions |  |
|  | Generator Monitoring Parameters The system shall monitor, at a minimum, the following parameters: |  |
|  | Generator Operating Parameters - Generator running status (ON/OFF) - Engine running hours - Engine RPM - Generator load (%) - Engine temperature - Battery voltage - Battery health and charging status - Fuel consumption rate - Fuel level and remaining fuel autonomy |  |
|  | Electrical Parameters - Generator output voltage (Three Phase) - Generator output current (Three Phase) - Frequency (Hz) - Active power (kW) - Apparent power (kVA) - Power factor - Energy generation (kWh) |  |
|  | Grid Monitoring The system shall provide continuous monitoring of the utility grid, including: - Grid availability status - Grid phase voltages - Grid phase currents - Grid frequency - Grid energy consumption (kWh) - Automatic detection of grid failure and restoration |  |
|  | Fuel Management The system shall provide advanced fuel management capabilities, including: - Continuous fuel level monitoring - Real-time fuel consumption monitoring - Fuel refill detection and logging - Detection of abnormal fuel drops - Fuel theft detection and alerting - Fuel consumption analytics and historical reports |  |
|  | Security and Access Monitoring The system shall provide security monitoring features including: - Generator door open/close monitoring - Unauthorised access alerts - GPS location monitoring - Event logging and audit trail |  |
|  | Remote Control Capability (Optional) The proposed solution may provide remote operational control features, including: - Remote Start of generator - Remote Stop of generator - Remote acknowledgement of alarms - Secure access control with user permissions |  |
|  | Alerts and Notifications The system shall support configurable alarms and automatic notifications through: - Web dashboard alerts - Email notifications - Popup notifications |  |
|  | Alarm conditions shall include, but not be limited to: - Low fuel level - Sudden fuel drop - Generator fault - Engine over-temperature - Battery low voltage - Grid failure - Grid restoration - Door opening - Communication loss - Unauthorised access |  |
|  | Dashboard and User Interface The system shall provide: - Centralised dashboard for all monitored sites - Real-time status overview - Historical trends and analytics - Graphical presentation of monitored parameters - Site map and asset location view - Multi-user access with role-based permissions The dashboard shall be accessible through standard web browsers without requiring specialised software installation. |  |
|  | Reporting and Analytics The system shall provide automated reporting and analytics capabilities including: - Fuel consumption reports - Generator utilisation reports - Running hours reports - Electricity generation reports - Electricity consumption reports - Maintenance reports - Alarm and event reports - Historical trends and performance analytics Historical operational data shall be stored for a minimum period of eighteen (18) months. |  |
|  | Communication and Connectivity The system shall: - Operate over GSM / 4G communication networks - Include all communication hardware - Include SIM card and communication services where applicable - Provide secure cloud hosting |  |
|  | Expandability The solution shall support future integration with additional sensors and assets, including but not limited to: - Temperature sensors - Humidity sensors - Environmental sensors - Additional power and energy monitoring devices - Battery banks, UPS systems and inverters. |  |
|  | Installation and Support The supplier shall provide: - Technical Site Survey (TSS) - Hardware supply and installation - System commissioning and testing - User training - Technical support and maintenance services - One (1) year warranty on supplied hardware(SLA from second year and on). |  |
|  | Expected Benefits The proposed solution should enable the organisation to: - Improve generator availability and operational reliability - Reduce fuel losses and fuel theft - Improve preventive maintenance planning - Increase operational visibility across all sites - Reduce operational expenditure (OPEX) - Improve security and asset protection - Provide management with real-time operational information and analytics |  |
|  | Warranty: 12 months |  |