## Takeoff__SUBSTUCTURE (hidden)
SUBSTUCTURE
Site Clearance
Topsoil excavation
Pit Excavation
Trench Excavation
Blinding in pit
Reinf in pit
conc in col base
mass conc in trs
Reinf in col
Formwork to sides of col
Conc in col
Blockwork
HCF
Formwork to sides of Bed
Conc in floor bed
Site Clearance
[6 empty] | L | B
[6 empty] | 20.3 | 17.625
[6 empty] | 1 | 1
[6 empty] | 21.3 | 18.625
21.3
18.625
396.7125
Pit Excavation
Pit 1 depth wrkup
[5 empty] | coln part | 0.45
[5 empty] | coln base | 0.3
[5 empty] | blinding | 0.05
0.8
Pit 2 depth workup
[5 empty] | coln part | 0.45
[5 empty] | coln base | 0.3
[5 empty] | blinding | 0.05
0.8
L |  | 24 | 1.2
B |  |  | 1.2
D |  |  | 0.8 | 27.648 | (Pit 1
L |  | 4 | 1.5
B |  |  | 1.5
D |  |  | 0.8 | 7.2 | (Pit 2
34.848
Trench Excavation
Trs wrkup
A-A
0.375
1.7
1.275
3.35
less pit width
[5 empty] | 1 | 1.2 | 1.2
0
1.2
[5 empty] | A-A | length | 2.15
B-B
0.425
1.55
3.025
5
less pit width
[5 empty] | 0.5 | 1.2 | 0.6
0
0.6
[5 empty] | B-B | length | 4.4
[5 empty] | C-C |  | 0.375
1.7
1.275
3.35
less pit width
0
[5 empty] | C-C | length | 3.35
[5 empty] | D-D |  | 2.8
1.4
4.2
[5 empty] | 1 | 1.2 | 1.2
[5 empty] | D-D | length | 3
[5 empty] | E-E |  | 2
0.425
1.55
3.025
1.475
8.475
[5 empty] | 1.5 | 1.2 | 1.8
[5 empty] | E-E | 0 | 6.675
[5 empty] | F-F |  | 2.8
1.4
4.2
[5 empty] | 0.5 | 1.2 | 0.6
[5 empty] | F-F | length | 3.6
[5 empty] | G-G |  | 2
0.425
1.55
3.15
2.05
9.175
[5 empty] | 2 | 1.5 | 3
[5 empty] | G-G | length | 6.175
[5 empty] | H-H |  | 1.4
2.8
1.4
5.6
[5 empty] | 2 | 1.2 | 2.4
[5 empty] | H-H | length | 3.2
[5 empty] | J-J |  | 1.4
2.8
1.4
0.375
1.275
0.425
1.55
3.025
1.475
2.05
15.775
[5 empty] | 1 | 1.2 | 1.2
[5 empty] | 2 | 1.5 | 3
4.2
[5 empty] | J-J | length | 11.575
[5 empty] | K-K |  | 1.7
1.275
0.425
3.4
0
[5 empty] | K-K | length | 3.4
[5 empty] | L-L |  | 2.8
1.4
0.375
1.7
1.275
0.425
1.55
3.025
0.375
1.7
1.275
0.425
1.55
3.025
20.9
[5 empty] | 3 | 1.2 | 3.6
[5 empty] | L-L | length | 17.3
1-1.
4.65
4.65
less
[5 empty] | 1 | 1.2 | 1.2
[5 empty] | 1-1. | length | 3.45
2-2
0.95
2.775
0.375
2.1
1.5
3.1
10.8
less
[5 empty] | 2 | 1.2 | 2.4
2.4
[5 empty] | 2-2 | length | 8.4
3-3
4.65
4.65
0
0
[5 empty] | 3-3 | length | 4.65
4-4
1
1.825
1.875
0.95
2.775
0.375
2.1
4.65
15.55
less
[5 empty] | 4 | 1.2 | 4.8
4.8
[5 empty] | 4-4 | 0 | 21.5
5-5
1.5
3.1
4.6
less
[5 empty] | 1 | 1.2 | 1.2
1.2
[5 empty] | 5-5 | 0 | 3.4
6-6
3.5
3.1
6.6
less
[5 empty] | 1 | 1.2 | 1.2
1.2
[5 empty] | 6-6 | 0 | 5.4
[5 empty] | 7-7 |  | 1
1.825
1
3.825
less
[5 empty] | 0.5 | 1.2 | 0.6
0.6
[5 empty] | 7-7 | 0 | 3.225
8-8
2.1
4.65
1.5
3.1
11.35
less
[5 empty] | 1.5 | 1.5 | 2.25
[5 empty] | 0.5 | 1.2 | 0.6
2.85
[5 empty] | 8-8 | 0 | 8.5
9-9
3.15
3.15
6.3
less
0
0
[5 empty] | 9-9 | 0 | 6.3
10-10
1.825
1.875
0.95
2.1
4.65
1.5
3.1
16
less
[5 empty] | 1.5 | 1.2 | 1.8
[5 empty] | 1 | 1.5 | 1.5
3.3
[5 empty] | 10-10 | 0 | 12.7
11-11
3.15
2.1
4.65
9.9
less
[5 empty] | 1 | 2 | 2
[7 empty] | 2 |  |  | 0.33333
0.5
[5 empty] | 11-11 | 0 | 7.9
i | [5 empty] | A-A | 2.15
[6 empty] | B-B | 4.4
[6 empty] | C-C | 3.35
[6 empty] | D-D | 3
[6 empty] | E-E | 6.675
[6 empty] | F-F | 3.6
[6 empty] | G-G | 6.175
[6 empty] | H-H | 3.2
[6 empty] | J-J | 11.575
[6 empty] | K-K | 3.4
[6 empty] | L-L | 17.3
[6 empty] | 1-1. | 3.45
[6 empty] | 2-2 | 4.65
[6 empty] | 4-4 | 21.5
[6 empty] | 5-5 | 3.4
[6 empty] | 6-6 | 5.4
[6 empty] | 7-7 | 3.225
[6 empty] | 8-8 | 8.5
[6 empty] | 9-9 | 6.3
[6 empty] | 10-10 | 12.7
[6 empty] | 11-11 | 7.9
[5 empty] | Total trs len |  | 141.85
[5 empty] | trs depth | 0.45
0.3
0.75
len |  |  | 141.85
brdth |  |  | 0.45
dpth |  |  | 0.75
47.8744
Blinding in pit
|  | 24 | 1.2
1.2
|  |  | 0.05 | 1.728 |  |  |  |  | 56.55
|  | 4 | 1.5
1.5
|  |  | 0.05 | 0.45
2.178
Reinf in pit
[5 empty] | 1.2 |  | No.
[5 empty] | 0.2 | 6 | 7
[5 empty] | 1.5 |  | No.
[5 empty] | 0.2 | 7.5 | 8.5
[5 empty] | Len | 1.2 | 1.5
[5 empty] | less cover | 0.05 | 0.05
[6 empty] | 1.15 | 1.45
[5 empty] | add bends | 0.2 | 0.2
[6 empty] | 1.35 | 1.65
| 7 | 24 | 1.35 | 226.8
| 8.5 | 4 | 1.65 | 56.1
|  |  |  | 282.9 | 1.562 | 16mm D. Bar
|  |  |  | 441.8898 | kg | 0.44189
conc in col base
|  | 24 | 1.2
1.2
|  |  | 0.3 | 10.368
|  | 4 | 1.5
1.5
|  |  | 0.3 | 2.7
13.068
mass conc in trs
141.85
0.45
0.3
19.1497
Reinf in col
[6 empty] | ht of reinf col | links
[5 empty] | bend | 0.3
[5 empty] | base | 0.25
[5 empty] | col | 0.9 | 7 | 8
[5 empty] | bed | 0.15
[5 empty] | overlap | 0.6
2.2
| 6 | 22 | 2.2 | 290.4
| 6 | 4 | 2.2 | 52.8
| 6 | 4 | 2.2 | 52.8
|  |  |  | 343.2 | 1.56 | 16mm D
|  |  |  | 535.392 | kg | 0.53539
LINKS
[5 empty] | col length | 0.3 | col width | 0.175
[5 empty] | less cover | 0.05 | less cover | 0.05
[6 empty] | 0.25 |  | 0.125
[5 empty] | four sides | 2 | circular | 2
[6 empty] | 0.5 |  | 0.25
[5 empty] | add bends | 0.05 | add bends | 0.05
[6 empty] | 0.55 |  | 0.3
0.85
CIRCULAR COL
[5 empty] | col diameter | 0.3
[5 empty] | less cover | 0.05
0.25
[5 empty] | circular | 3.142
0.7855
[5 empty] | add bends | 0.1
0.8855
0.8855
| 8 | 22 | 0.85 | 149.6
| 8 | 4 | 0.85 | 27.2
| 8 | 4 | 0.8855 | 28.336
|  |  |  | 176.8 | 0.617
|  |  |  | 109.0856 | kg | 0.10909
Formwork to sides of col
[5 empty] | 2 | 0.3 | 0.6
[5 empty] | 2 | 0.175 | 0.35
0.95
|  | 22 | 0.95 | 20.9 | 3.142 | 0.3 | 0.9426
|  | 4 | 0.95 | 3.8
|  | 4 | 0.9426 | 3.7704
28.4704
Conc in col
ht of col
0.45
| 0.7855 | 4 | 0.3 |  |  | 0.45
|  |  | 0.3 |  |  | 0.9
|  |  | 0.9 | 0.2545 |  | Ddt fillg
|  | 22 | 0.3 |  |  | 0.12725
|  |  | 0.175 |  |  | 0.51975
|  |  | 0.9 | 1.0395 |  | 0.21
|  | 4 | 0.3 |  |  | 0.647
0.175
|  |  | 0.9 | 0.189
1.483
Blockwork
[5 empty] | A-A |  | 3.35
less COLUMN
[5 empty] | 1 | 0.3 | 0.3
0
0.3
[5 empty] | A-A | length | 3.05
[5 empty] | B-B |  | 5
less COLUMN
0
[5 empty] | 0.5 | 0.3 | 0.15
0.15
[5 empty] | B-B | length | 4.85
[5 empty] | C-C |  | 3.35
less COLUMN
0
[5 empty] | 5 | 0.15 | 0.75
0.75
[5 empty] | C-C | length | 2.6
[5 empty] | D-D |  | 4.2
less COLUMN
[5 empty] | 1 | 0.3 | 0.3
[5 empty] | D-D | length | 3.9
[5 empty] | E-E |  | 8.475
less COLUMN
[5 empty] | 1.5 | 0.3 | 0.45
[5 empty] | E-E |  | 8.025
[5 empty] | F-F |  | 4.2
less COLUMN
[5 empty] | 0.5 | 0.3 | 0.15
[5 empty] | F-F |  | 4.05
[5 empty] | G-G |  | 9.175
less COLUMN
[5 empty] | 2 | 0.3 | 0.6
[5 empty] | G-G |  | 8.575
[5 empty] | H-H |  | 5.6
less COLUMN
[5 empty] | 2.5 | 0.3 | 0.75
[5 empty] | H-H |  | 4.85
[5 empty] | J-J |  | 15.775
less COLUMN
[5 empty] | 4 | 0.3 | 1.2
[5 empty] | J-J |  | 14.575
[5 empty] | K-K |  | 3.4
less COLUMN
[6 empty] | 0.3 | 0
[5 empty] | K-K |  | 3.4
[5 empty] | L-L |  | 20.9
less COLUMN
[5 empty] | 3 | 0.3 | 0.9
[5 empty] | L-L |  | 20
[5 empty] | 1-1. |  | 4.65
less COLUMN
[5 empty] | 1 | 0.175 | 0.175
0
0.175
[5 empty] | 1-1. |  | 4.475
[5 empty] | 2-2 |  | 10.8
less COLUMN
0
[5 empty] | 2 | 0.175 | 0.35
0.35
[5 empty] | 2-2 |  | 10.45
[5 empty] | 3-3 |  | 4.65
less COLUMN
0
[5 empty] | 0 | 0.15 | 0
0
[5 empty] | 3-3 |  | 4.65
[5 empty] | 4-4 |  | 15.55
less COLUMN
[5 empty] | 3.5 | 0.175 | 0.6125
[5 empty] | 4-4 |  | 14.9375
[5 empty] | 5-5 |  | 4.6
less COLUMN
[5 empty] | 1 | 0.175 | 0.175
0
0.175
[5 empty] | 5-5 |  | 4.425
[5 empty] | 6-6 |  | 6.6
less COLUMN
[5 empty] | 1 | 0.3 | 0.3
[5 empty] | 6-6 |  | 6.3
[5 empty] | 7-7 |  | 3.825
less COLUMN
[5 empty] | 1 | 0.175 | 0.175
[5 empty] | 7-7 |  | 3.65
[5 empty] | 8-8 |  | 11.35
less
[5 empty] | 2 | 0.175 | 0.35
0.35
[5 empty] | 8-8 |  | 11
[5 empty] | 9-9 |  | 6.3
less
[6 empty] | 0.15 | 0
0
[5 empty] | 9-9 |  | 6.3
[5 empty] | 10-10 |  | 16
less
[5 empty] | 1 | 0.175 | 0.175
[5 empty] | 2 | 0.175 | 0.35
0.525
[5 empty] | 10-10 |  | 15.475
[5 empty] | 11-11 |  | 9.9
less
[5 empty] | 1 | 0.3 | 0.3
0.3
[5 empty] | 11-11 |  | 9.6
LEMGTH OF BLOCKWORK
[5 empty] | A-A | 3.05
[5 empty] | B-B | 4.85
[5 empty] | C-C | 2.6
[5 empty] | D-D | 3.9
[5 empty] | E-E | 8.025
[5 empty] | F-F | 4.05
[5 empty] | G-G | 8.575
[5 empty] | H-H | 4.85
[5 empty] | J-J | 14.575
[5 empty] | K-K | 3.4
[5 empty] | L-L | 20
[5 empty] | 1-1. | 4.475
[5 empty] | 2-2 | 10.45
[5 empty] | 3-3 | 4.65
[5 empty] | 4-4 | 14.9375
[5 empty] | 5-5 | 4.425
[5 empty] | 6-6 | 6.3
[5 empty] | 7-7 | 3.65
[5 empty] | 8-8 | 11
[5 empty] | 9-9 | 6.3
[5 empty] | 10-10 | 15.475
[5 empty] | 11-11 | 9.6
169.1375
Blockwork
169.1375
0.9
152.2237
Ddt fillg
22.8336
HCF
|  |  | 2.375 |  | 2.85 | 0.15
|  |  | 0.9 | 2.1375 | 1.8 | 0.15
|  |  | 2.375 |  | 3 | 0.15
|  |  | 1.55 | 3.6812 | 3 | 0.15
|  |  | 4.55 |  | 4.8 | 0.15
|  |  | 4.2 | 19.11 | 3 | 0.15
|  |  | 2.675 |  | 3 | 0.15
|  |  | 1.55 | 4.1463 | 2.4 | 0.15
|  |  | 3.275 |  | 12.6 | 0.15
|  |  | 3.75 | 12.2812 | 1.5 | 0.15
|  |  | 3.75 |  | 4.2 | 0.15
|  |  | 2.025 | 7.5938 | 4.2 | 0.15
|  |  | 1.55 |  | 4.2 | 0.15
|  |  | 3.15 | 4.8825 | 1.8 | 0.15
|  |  | 4.2 |  | 6 | 0.15
|  |  | 3.725 | 15.645 | 1.8 | 0.15
|  |  | 3 |  | 4.2 | 0.15
|  |  | 3.1 | 9.3 | 3.6 | 0.15
9.125
|  |  | 1.2 | 10.95
3.616
|  |  | 3.95 | 14.2832
4.2
|  |  | 1.25 | 5.25
4
|  |  | 0.375 | 1.5
4.2
|  |  | 3.616 | 15.1872
3.15
|  |  | 0.9 | 2.835
4.275
|  |  | 4.3 | 18.3825
4.275
|  |  | 3.075 | 13.1456
4.275
|  |  | 3.075 | 13.1456
3.15
|  |  | 3.15 | 9.9225
6.45
|  |  | 3.225 | 20.8012
4.3
|  |  | 4.275 | 18.3825
2.8
|  |  | 1.4 | 3.92
2.8
|  |  | 1.4 | 3.92
4.2
|  |  | 4.2 | 17.64
248.0429
|  |  | X | 0.45
111.6193
|  |  |  | 111.6193 | m3
Formwork to sides of Bed
|  | 2 | 20.15 | 40.3
|  | 2 | 17.45 | 34.9
75.2
|  |  |  | 75.2 | m
Conc in floor bed
7.425
|  |  | 17.475 | 129.7519 |  |  |  |  | 5.85
|  |  | 4.6 | [5 empty] | 0.3
|  |  | 12.7 | 58.42 |  |  |  |  | 6.15
12.7
|  |  | 3.725 | 47.3075
4.725
|  |  | 8.641 | 40.8287
|  |  |  | 235.4794 |  | 470.9588
0.15
35.3219
|  |  |  | 35.3219 | m3
[6 empty] | Backfilling |  | R.F.S
[5 empty] | Pit Excavation | 34.848 | Blinding in pit | 2.178
[5 empty] | Trench Excavation | 47.8744 | conc in col base | 13.068
[7 empty] | mass conc in trs | 19.1497
[7 empty] | Conc in col | 0.647
[7 empty] | Blockwork | 22.8336
[6 empty] | 82.7224 |  | 57.8763
24.8461
[5 empty] | Mesh | Less Blockwrk thkness
[5 empty] | 7.425 | 0.15 | 7.275
[5 empty] | 17.475 | 0.15 | 17.325
[5 empty] | 4.6 | 0.15 | 4.45
[5 empty] | 12.7 | 0.15 | 12.55
[5 empty] | 12.7 | 0.15 | 12.55
[5 empty] | 3.725 | 0.15 | 3.575
[5 empty] | 4.725 | 0.15 | 4.575
[5 empty] | 8.641 | 0.15 | 8.491
57.725
9
519.525
7.275
|  |  | 17.325 | 126.0394
4.45
|  |  | 12.55 | 55.8475
12.55
|  |  | 3.575 | 44.8662
4.575
|  |  | 8.491 | 38.8463
|  |  |  | 265.5994 | m2
Plaster and Paint
[5 empty] | 2 | 20.3 | 40.6
[5 empty] | 2 | 17.625 | 35.25
2
77.85
77.85
0.6
|  |  |  | 46.71 | m2

## Take-off__Superstrcture (hidden)
SUPERSTRUCTURE
Reinf in col
Formwork to sides of col
Concrete in Column
Blockwork
Concrete Beam
Roof Timber memebers
Roofing sheet
Window / Door frames
Louvre Carriers
Louvre Blades
Plaster
Floor finish
Painting
[5 empty] | Reinf in col | C1 rod length | links - divide by centers |  | C2 rod length
[6 empty] | 2.5 |  |  | 2.5
[6 empty] | 0.3 |  |  | 0.3
[6 empty] | 0.15 |  |  | 0.15
[6 empty] | 0.6 |  |  | 0.6
[6 empty] | 3.55 |  |  | 3.55
[5 empty] | ctrs | 0.2 | 18.75 |  | 0.2 | 18.75
C1
[5 empty] | length of links | 0.3 |  | length of links | 0.3 | 0.175
[5 empty] | less cover | 0.05 |  | less cover | 0.05 | 0.05
[6 empty] | 0.25 |  |  | 0.25 | 0.125
red means constant |  |  |  |  | round | 0.7855 |  | four sides | 2 | 2
[9 empty] | 0.5 | 0.25
[5 empty] | add overlap | 0.1 |  | add bends | 0.05 | 0.05
[6 empty] | 0.8855 |  |  | 0.55 | 0.3
| 6 | 4 | 3.55 | 85.2 | [5 empty] | 0.85
| 6 | 22 | 3.55 | 468.6
| 6 | 4 | 3.55 | 85.2
|  |  |  | 639 | 1.56 | 16mm diameter rod
|  |  |  | 996.84 | kg
0.99684
| 19 | 4 | 0.8855 | 67.298
| 19 | 22 | 0.85 | 355.3
| 19 | 4 | 0.85 | 64.6
|  |  |  | 487.198 | 0.617 | 10mm diameter rod
|  |  |  | 300.6012 | Kg
Formwork to sides of col
[5 empty] | Size of col |  |  |  | Ht of Col C1
[5 empty] | Diameter | 0.3 |  |  | 2.5
0.9426
[5 empty] | L | 0.3
[5 empty] | B | 0.175 | 0.95 |  | 2.5
|  | 4 | 0.9426 | [5 empty] | Ht of Col C2
|  |  | 2.5 | 9.426
|  | 26 | 0.95 | [5 empty] | 2.5
|  |  | 2.5 | 61.75
|  |  |  | 71.176 | m2 |  |  |  | 2.5
Concrete in Column
| 0.7855 | 4 | 0.3
0.3
|  |  | 2.5 | 0.70695
|  | 26 | 0.3
0.175
|  |  | 2.5 | 3.4125
4.1195
Blockwork
[5 empty] | A-A |  | 3.35
less COLUMN
0
0
terrace
0
[5 empty] | A-A | length | 3.35
[5 empty] | B-B |  | 5
less COLUMN
0
0
0
[5 empty] | B-B | length | 5
[5 empty] | C-C |  | 3.35
less COLUMN
0
0
0
0
[5 empty] | C-C | length | 3.35
[5 empty] | D-D |  | 4.2
less COLUMN
0
0
0
[5 empty] | D-D | length | 4.2
[5 empty] | E-E |  | 8.475
less COLUMN
0
[5 empty] | E-E |  | 8.475
[5 empty] | F-F |  | 4.2
less COLUMN
0
[5 empty] | F-F |  | 4.2
[5 empty] | G-G |  | 9.175
less COLUMN
0
0
0
[5 empty] | G-G |  | 9.175
[5 empty] | H-H |  | 5.6
less COLUMN
0
0
0
[5 empty] | H-H |  | 5.6
[5 empty] | J-J |  | 1.4
2.8
1.4
0.375
1.275
0.425
1.55
3.025
12.25
0
[5 empty] | J-J | length | 12.25
[5 empty] | K-K |  | 1.7
1.275
0.425
3.4
0
[5 empty] | K-K | length | 3.4
[5 empty] | L-L |  | 2.8
1.4
0.375
1.7
1.275
0.425
1.55
3.025
12.55
0
[5 empty] | L-L | length | 12.55
[5 empty] | 1-1. |  | 4.65
less COLUMN
0
0
0
0
[5 empty] | 1-1. |  | 4.65
[5 empty] | 2-2 |  | 10.8
less COLUMN
0
0
0
[5 empty] | 2-2 |  | 10.8
3-3
less COLUMN
0
0
0
[5 empty] | 3-3 |  | 0
[5 empty] | 4-4 |  | 15.55
less COLUMN
0
[5 empty] | 4-4 |  | 31.1
[5 empty] | 5-5 |  | 4.6
less COLUMN
0
0
0
0
[5 empty] | 5-5 |  | 9.2
[5 empty] | 6-6 |  | 6.6
less COLUMN
0
[5 empty] | 6-6 |  | 6.6
[5 empty] | 7-7 |  | 3.825
less COLUMN
0
[5 empty] | 7-7 |  | 3.825
8-8
0
less
0
0
[5 empty] | 8-8 |  | 0
LEMGTH OF BLOCKWORK
[5 empty] | A-A | 3.35
[5 empty] | B-B | 5
[5 empty] | C-C | 3.35
[5 empty] | D-D | 4.2
[5 empty] | E-E | 8.475
[5 empty] | F-F | 4.2
[5 empty] | G-G | 9.175
[5 empty] | H-H | 5.6
[5 empty] | J-J | 12.25
[5 empty] | K-K | 3.4
[5 empty] | L-L | 12.55
[5 empty] | 1-1. | 4.65
[5 empty] | 2-2 | 10.8
[5 empty] | 3-3 | 0
[5 empty] | 4-4 | 31.1
[5 empty] | 5-5 | 9.2
[5 empty] | 6-6 | 6.6
[5 empty] | 7-7 | 3.825
[5 empty] | 8-8 | 0
137.725
Blockwork
Gable
|  |  | 137.725 |  |  | AV HT
|  |  | 2.85 |  |  |  | 0
392.5163
| 4 | 0.5 | 0
|  |  | 2.382 |  |  |  |  | 0 | 0
|  |  |  | 0 | Gable
[5 empty] | Ddt Opening |  | L | B
[5 empty] | w1 | 4 | 0.75 | 1.5 | 4.5
[5 empty] | w2 | 10 | 1.2 | 1.8 | 21.6
[5 empty] | w3 | 1 | 1.2 | 4.225 | 5.07
[5 empty] | w4 | 1 | 0.95 | 0.9 | 0.855
[5 empty] | HLW | 1 | 0.95 | 1.8 | 1.71
[6 empty] | 1 | 0.75 | 0.767 | 0.57525
[5 empty] | D 1 | 5 | 2.1 | 0.75 | 7.875
[5 empty] | D2 | 6 | 2.1 | 0.95 | 11.97
[5 empty] | D3 | 1 | 2.1 | 1.5 | 3.15 | [5 empty] | 2.7
57.3052
137.725
2.85
392.5163
57.3052
|  |  |  | 335.211 | Blockwork
Concrete Beam
[6 empty] | No. of links | length of link
|  |  | 137.725 |  |  | 2167.3667 | 1.1
0.15
0.3
|  |  |  | 6.1976 | m3
Reinf. In beam
|  | 4 | 137.725 | 550.9 | 1.576
868.2184
|  | 2168 | 1.1
|  |  |  | 2384.8 | 0.222
529.4256
Formwork to sides and soffit of beam
[6 empty] | 2 | 0.3 | 0.6 | sied
[8 empty] | 0.15 | soffit
|  |  | 137.725 |  |  |  |  | 0.75
0.75
|  |  |  | 103.2937 | m2
Window / Door frames
[5 empty] | Ddt Opening |  | No. of Vert | VERT | HOR
[5 empty] | w1 |  | 5 | 1.5 | 0.75 | 0
[5 empty] | w2 |  | 4 | 1.8 | 1.2 | 0
[5 empty] | w3 |  | 3 | 4.225 | 1.2 | 0
[5 empty] | w4 |  | 3 | 0.9 | 0.95 | 0
[5 empty] | HLW |  | 2 | 1.8 | 0.95 | 0
[5 empty] | D 1 |  |  |  |  | 0
[5 empty] | D2 | 1 | 2 | 2.1 | 1.5 | 7.8
[5 empty] | D3 | 6 | 2 | 2.1 | 0.9 | 36
[5 empty] | D2 | 4 | 2 | 2.1 | 0.75 | 22.8
58.8
|  |  | 0 | 0 | Window frame
|  |  | 58.8 | 58.8 | Door frame
WIMDOW / DOOR STOP
[5 empty] | Ddt Opening |  | No. of Vert | VERT | HOR
[5 empty] | 0 |  | 5 | 0 |  | 0
[5 empty] | 0 |  | 4 | 0 | 1.1 | 0
[5 empty] | 0 |  | 3 | 0 | 0 | 0
[5 empty] | 0 |  | 3 | 0 | 0 | 0
[5 empty] | m3 |  | 2 | 0 | 0 | 0
[5 empty] | Reinf. In beam |  |  |  |  | 0
[5 empty] | D2 | 1 | 2 | 2.05 | 1.4 | 7.5
[5 empty] | D3 | 6 | 2 | 2.05 | 0.8 | 34.2
[5 empty] | D2 | 4 | 2 | 2.05 | 0.75 | 22.4
56.6
hwl
Louvre Blades
| 4 | 4 | 12 | 192
| 10 | 3 | 11 | 330
| 1 | 2 | 11 | 22
| 1 | 2 | 9 | 18
| 1 | 1 | 4 | 4
566
[6 empty] | 12 | 11 | 9.6667 | 4
Louvre Carriers
w1 |  | 4 | 4 | 16
w2 |  | 10 | 3 | 30
|  | 1 | 2 | 2
w3 |  | 1 | 2 | 2
|  | 1 | 1 | 1
w4
Plaster
670.422
Floor tile
BEDROOM |  |  | 5
|  |  | 4.65 | 23.25 | G.R.
2.675
|  |  | 2 | 5.35 | G.R. CLOSET
4.45
|  |  | 4.425 | 19.6912 | BEDRM 2
4.45
|  |  | 4.425 | 19.6913 | BEDRM 3
6.6
|  |  | 6.125 | 40.425 | LIVGRM |  | 600 X 600 PORCELAIN SP
3
|  |  | 3 | 9 | STUDY
12.725
|  |  | 1.55 | 19.7237 | COR
6.6
|  |  | 0.375 | 2.475 | COR
3.15
|  |  | 1.2 | 3.78 | COR
3.4
|  |  | 1.35 | 4.59
4.05
|  |  | 3.575 | 14.4787 | DIN
|  | 3 | 0.15
|  |  | 0.9 | 0.405 | DR OPENING
162.86
2.95
|  |  | 1.55 | 4.5725 | BATHRM
2.95
|  |  | 1.55 | 4.5725 | BATHRM
2.675
|  |  | 1.2 | 3.21 | BATHRM
2.675
|  |  | 1.85 | 4.9487 | BATHRM
|  | 4 | 0.15
|  |  | 0.75 | 0.45
0.15
|  |  | 1.2 | 0.18
17.9337
4.05
|  |  | 2.325 | 9.4162 | PANTRY
4.5
|  |  | 4.05 | 18.225 | KITCHEN
4.05
|  |  | 1.25 | 5.0625 | STORE
|  | 3 | 0.15
|  |  | 0.9 | 0.405
33.1088
3.6
|  |  | 2 | 7.2 | TERRACE | [5 empty] | 1.725
6.75
|  |  | 3.525 | 23.7937 | PORCH
30.9937
162.86
17.9337
33.1088
[5 empty] | 30.9937 | [6 empty] | tread
244.8962
[12 empty] | 2.05 | 1.475 | 0.375
[12 empty] | 0.6 | 2.05 | 2.1
[5 empty] | Wall tiles | [6 empty] | 2.65 | 0.6 | 4.65
[5 empty] | 2 | 2.675 | 5.35 | [5 empty] | 4.125 | 0.6
[5 empty] | 2 | 1.85 | 3.7 | [6 empty] | 0.3
[7 empty] | 9.05 | [6 empty] | 8.025
[5 empty] | 2 | 2.675 | 5.35 | [6 empty] | 14.8
[5 empty] | 2 | 1.85 | 3.7
[7 empty] | 9.05 |  |  |  |  | 2.05 | 1.475 | 0.375
[5 empty] | 2 | 2.95 | 5.9 |  |  |  |  | 0.3 | 2.05 | 2.1
[5 empty] | 2 | 1.55 | 3.1 |  |  |  |  | 2.35 | 0.3 | 4.65
[7 empty] | 9 | [5 empty] | 3.825 | 0.3
[5 empty] | 2 | 2.95 | 5.9 | [6 empty] | 7.425
[5 empty] | 2 | 1.55 | 3.1
9
13.6
|  | 2 | 9.05
|  |  | 1.2 | 21.72
|  | 2 | 9.05
|  |  | 1.2 | 21.72
|  |  |  | 86.88 | [9 empty] | 28.4
|  | 4 | 0.75 |  | ddt dr opgn
1.2
|  |  |  | 3.6 | [7 empty] | riser
|  |  |  | 83.28 | m2
CEILING FINISHES
23.25
5.35
19.6912
19.6913
9
19.7237
2.475
3.78
4.59
14.4787
0.405
9.4162
18.225
5.0625
0.405
|  |  |  | 155.5437 | PLASTER BOARD
|  |  |  | 17.9337 | T&G PLASTIC |  | 173.4775
30.9937
40.425
|  |  |  | 40.425 | POP |  | 244.8963
PAINTING
Isolated Columns
| 4 | 3.142 | 0.3
2.5
9.426
Painting to hardwwod
|  |  | 58.8 |  | Frames
0.25
14.7
|  | 1 | 3 |  | Doors
|  |  | 2.1 | 6.3
|  | 6 | 1.8
|  |  | 2.1 | 12.6
18.9
33.6
LINTELS
4.225

## Take-off__FIRST FLOOR (hidden)
SUPERSTRUCTURE
Reinf in col
Formwork to sides of col
Concrete in Column
Blockwork
Concrete Beam
Roof Timber memebers
Roofing sheet
Window / Door frames
Louvre Carriers
Louvre Blades
Plaster
Floor finish
Painting
[5 empty] | Reinf in col | C1 rod length | links - divide by centers |  | C2 rod length
[6 empty] | 2.55 |  |  | 2.55
[6 empty] | 0.225 |  |  | 0.225
[6 empty] | 0.6 |  |  | 0.6
[6 empty] | 3.375 |  |  | 3.375
[5 empty] | ctrs | 0.2 | 17.875 |  | 0.2 | 17.875
C1
[5 empty] | length of links | 0.3 |  | length of links | 0.3 | 0.175
[5 empty] | less cover | 0.05 |  | less cover | 0.05 | 0.05
[6 empty] | 0.25 |  |  | 0.25 | 0.125
red means constant |  |  |  |  | round | 0.7855 |  | four sides | 2 | 2
[9 empty] | 0.5 | 0.25
[5 empty] | add overlap | 0.1 |  | add bends | 0.1 | 0.1
[6 empty] | 0.8855 |  |  | 0.6 | 0.35
| 6 | 4 | 3.375 | 81 | [5 empty] | 0.95
| 6 | 22 | 3.375 | 445.5
| 6 | 4 | 3.375 | 81
|  |  |  | 607.5 | 1.567 | 16mm diameter rod
|  |  |  | 951.9525 | kg
| 18 | 26 | 0.8855 | 414.414
| 18 | 4 | 0.95 | 68.4
|  |  |  | 482.814 | 0.617 | 10mm diameter rod
|  |  |  | 297.8962 | Kg
Formwork to sides of col
[5 empty] | Size of col |  |  |  | Ht of Col C1
[5 empty] | Diameter | 0.3 |  |  | 2.55
[7 empty] | 0.9426 |  | 0.225
[5 empty] | L | 0.3
[5 empty] | B | 0.175 | 0.95 |  | 2.775
|  | 26 | 0.95 | [5 empty] | Ht of Col C2
|  |  | 2.775 | 68.5425 |  |  |  |  | 2.55
|  | 4 | 0.9426 | [5 empty] | 0.225
|  |  | 2.775 | 10.4629
|  |  |  | 79.0054 | m2 |  |  |  | 2.775
Concrete in Column
| 0.7855 | 26 | 0.3
0.3
|  |  | 2.775 | 5.1006
|  | 4 | 0.3
0.175
|  |  | 2.775 | 0.58275
5.6834
Blockwork
[5 empty] | A-A |  | 0.375
1.7
1.275
0.425
1.55
3.025
I | [6 empty] | 8.35
less COLUMN
0
0
terrace
0
[5 empty] | A-A | length | 8.35
B-B
less COLUMN
0
0
0
[5 empty] | B-B | length | 0
[5 empty] | C-C |  | 3.025
less COLUMN
0
0
0
0
[5 empty] | C-C | length | 3.025
D-D
less COLUMN
0
0
0
[5 empty] | D-D | length | 0
[5 empty] | E-E |  | 15.425
less COLUMN
0
[5 empty] | E-E |  | 15.425
F-F
less COLUMN
0
[5 empty] | F-F |  | 0
[5 empty] | G-G |  | 8.75
less COLUMN
0
0
0
[5 empty] | G-G |  | 8.75
H-H
less COLUMN
0
0
0
[5 empty] | H-H |  | 0
[5 empty] | J-J |  | 1.4
2.8
1.4
0.375
1.275
0.425
1.55
3.025
12.25
0
[5 empty] | J-J | length | 12.25
[5 empty] | K-K |  | 1.7
1.275
0.425
3.4
0
[5 empty] | K-K | length | 3.4
[5 empty] | L-L |  | 2.8
1.4
0.375
1.7
1.275
0.425
1.55
3.025
12.55
0
[5 empty] | L-L | length | 12.55
[5 empty] | 1-1. |  | 4.65
less COLUMN
0
0
0
0
[5 empty] | 1-1. |  | 4.65
[5 empty] | 2-2 |  | 10.8
less COLUMN
0
0
0
[5 empty] | 2-2 |  | 10.8
3-3
less COLUMN
0
0
0
[5 empty] | 3-3 |  | 0
[5 empty] | 4-4 |  | 15.55
less COLUMN
0
[5 empty] | 4-4 |  | 31.1
[5 empty] | 5-5 |  | 4.6
less COLUMN
0
0
0
0
[5 empty] | 5-5 |  | 9.2
[5 empty] | 6-6 |  | 6.6
less COLUMN
0
[5 empty] | 6-6 |  | 6.6
[5 empty] | 7-7 |  | 3.825
less COLUMN
0
[5 empty] | 7-7 |  | 3.825
8-8
0
less
0
0
[5 empty] | 8-8 |  | 0
LEMGTH OF BLOCKWORK
[5 empty] | A-A | 8.35
[5 empty] | B-B | 0
[5 empty] | C-C | 3.025
[5 empty] | D-D | 0
[5 empty] | E-E | 15.425
[5 empty] | F-F | 0
[5 empty] | G-G | 8.75
[5 empty] | H-H | 0
[5 empty] | J-J | 12.25
[5 empty] | K-K | 3.4
[5 empty] | L-L | 12.55
[5 empty] | 1-1. | 4.65
[5 empty] | 2-2 | 10.8
[5 empty] | 3-3 | 0
[5 empty] | 4-4 | 31.1
[5 empty] | 5-5 | 9.2
[5 empty] | 6-6 | 6.6
[5 empty] | 7-7 | 3.825
[5 empty] | 8-8 | 0
129.925
Blockwork
Gable
|  |  | 129.925 |  |  | AV HT
|  |  | 3.878 |  |  | 3.878 | 3.878
503.8491
|  | 0.5 | 0
|  |  | 2.382 |  |  |  |  | 0 | 0
|  |  |  | 0 | Gable
[5 empty] | Ddt Opening |  | L | B
[5 empty] | w1 | 3 | 0.75 | 1.5 | 3.375
[5 empty] | w2 | 11 | 1.2 | 1.8 | 23.76
[5 empty] | w3 |  |  |  | 0
[5 empty] | w4 | 1 | 1.2 | 2.725 | 3.27
[5 empty] | HLW |  |  |  | 0
[5 empty] | D 1 | 3 | 2.1 | 0.75 | 4.725
[5 empty] | D2 | 6 | 2.1 | 0.95 | 11.97
[5 empty] | D3 |  |  |  | 0
47.1
129.925
3.878
503.8491
47.1
|  |  |  | 456.7491 | Blockwork
Concrete Beam
[6 empty] | No. of links | length of link
|  |  | 129.925 |  |  | 2167.3667 | 1.1
0.15
0.3
|  |  |  | 5.8466 | m3
Reinf. In beam
|  | 4 | 129.925 | 519.7 | 1.576
819.0472
|  | 2168 | 1.1
|  |  |  | 2384.8 | 0.222
529.4256
Formwork to sides and soffit of beam
[6 empty] | 2 | 0.3 | 0.6 | sied
[8 empty] | 0.15 | soffit
|  |  | 129.925 |  |  |  |  | 0.75
0.75
|  |  |  | 97.4437 | m2
Window / Door frames
[5 empty] | Ddt Opening |  | No. of Vert | VERT | HOR
[5 empty] | w1 |  | 5 | 1.5 | 0.75 | 0
[5 empty] | w2 |  | 4 | 1.8 | 1.2 | 0
[5 empty] | w3 |  | 3 | 0 | 0 | 0
[5 empty] | w4 |  | 3 | 2.725 | 1.2 | 0
[5 empty] | HLW |  | 2 | 0 | 0 | 0
[5 empty] | D 1 |  |  |  |  | 0
[5 empty] | D2 | 6 | 2 | 2.1 | 0.9 | 36.6
[5 empty] | D3 | 3 | 2 | 2.1 | 0.75 | 17.1
[5 empty] | D2 |  | 2 | 0 | 0 | 0
17.1
WINDOW / DOOR STOP
[7 empty] | No. of Vert | VERT | HOR
[5 empty] | w1 |  | 5 | 0 | 0 | 0
[5 empty] | w2 |  | 4 | 0 | 0 | 0
[5 empty] | w3 |  | 3 | 0 | length of link | #VALUE!
[5 empty] | w4 |  | 3 | 0 | 1.1 | 0
[5 empty] | HLW |  | 2 | 0 | 0 | 0
[5 empty] | 0 |  |  |  |  | #VALUE!
[5 empty] | D 1 | 6 | 2 | 2.05 | 0.8 | 34.8
[5 empty] | D2 | 3 | 2 | 2.05 | 0.7 | 16.5
[5 empty] | D3 |  | 2 | 0 | 0 | 0
D2
16.5
|  |  | 0 | 0 | Window frame
|  |  | 17.1 | 17.1 | Door frame
hwl
Louvre Blades
| 3 | 4 | 12 | 144
| 11 | 3 | 11 | 363
| 0 | 2 | 11 | 0
| 1 | 2 | 9 | 18
| 0 | 1 | 4 | 0
525
[6 empty] | 12 | 11 | 9.6667 | 4
Louvre Carriers
w1 |  | 3 | 4 | 12
w2 |  | 11 | 3 | 33
|  | 0 | 2 | 0
w3 |  | 1 | 2 | 2
|  | 0 | 1 | 0
w4
Plaster
913.4983
Floor tile
BEDROOM |  |  | 5.5
|  |  | 5.175 | 28.4625 | MBR 1
2.875
|  |  | 2.675 | 7.6906 | MBR. CLOSET
6.75
|  |  | 5.525 | 37.2938 | MBR 2
3.525
|  |  | 2.65 | 9.3412 | MBR. CLOSET
4.45
|  |  | 4.425 | 19.6913 | BEDRM |  | 600 X 600
2.95
|  |  | 1.55 |  | CLOSET
4.35
|  |  | 3 | 13.05 | STUDY
11.4
|  |  | 1.95 | 22.23 | COR
3.4
|  |  | 1.35 | 4.59 | COR
6.8
|  |  | 6 | 40.8 | LIVING RM
|  | 8 | 0.15
|  |  | 0.96 | 1.152
|  |  |  | 0 | DIN
184.3014
2.875
|  |  | 2.675 | 7.6906 | BATHRM
3.525
|  |  | 2.65 | 9.3412 | BATHRM
2.95
|  |  | 1.55 | 4.5725 | BATHRM
|  |  |  | 0 | BATHRM
21.6044
4.6
|  |  | 4.525 | 20.815 | TERRACE | [6 empty] | 1.725
5.525
|  |  | 1.425 | 7.8731 | PORCH
28.6881
Wall tiles
[5 empty] | 2 | 2.675 | 5.35
[5 empty] | 2 | 2.875 | 5.75
11.1
[5 empty] | 2 | 3.525 | 7.05
[5 empty] | 2 | 2.65 | 5.3
12.35
[5 empty] | 2 | 2.95 | 5.9
[5 empty] | 2 | 1.55 | 3.1
9
|  | 1 | 11.1
|  |  | 1.2 | 13.32
|  | 1 | 12.35
|  |  | 1.2 | 14.82
|  | 1 | 9
|  |  | 1.2 | 10.8
77.88
|  | 3 | 0.75 |  | ddt dr opgn
1.2
2.7
|  |  |  | 75.18 | m2
CEILING FINISHES
|  |  |  | 40.8 | POP
|  |  |  | 143.5014 | PPLASTER BOARD
|  |  |  | 21.6044 | PLASTIC T&G
Isolated Columns
| 4 | 3.142 | 0.3
2.775
10.4629
Painting to hardwwod
|  |  | 17.1 |  | Frames
0.25
4.275
|  | 1 | 1.8 |  | Doors
|  |  | 2.1 | 3.78
3.78
8.055
SOH
CAH
[6 empty] | H |  | O | TOA
30
A
[8 empty] | sin 30 = | 2.382
H
[8 empty] | H= | 4.764
15 x 40mm Planted door stop in Redwood
|  | 2 | 2.1 | 4.2
|  |  |  | 17.1 | 20 x 20mm Glazing beads
10 x 50mm Batten in Redwood
0
38X38mm Moulded cornix
20 x 75mm Skirting, once splayed
| 2 | 2 | 1.125
|  |  | 2.1 | 9.45 | General Surfaces
| 12 | 2 | 0.8
|  |  | 2.1 | 40.32 | [6 empty] | 2.4
| 6 | 2 | 0.65
|  |  | 2.1 | 16.38
66.15
2.2
0.05
2.25
0.5
0.55
1.125
0.55
0.55
0.025
1.125
2.25

## Cover
PROPOSED BILL OF QUANTITIES FOR THE CONSTRUCTION OF ASSAY CENTRE FOR GOLDBOD

## prelims
Item | Description | Qty | Unit | Rate | Amount
BILL No. 1: PRELIMINARIES
A10: PROJECT PARTICULARS
Name:
A | GOLDBOD NATIONAL ASSAY CENTRE
Item
B | Location:
| ACCRA, GHANA |  | Item
C | Employer:
GOLDBOD
D | Consultant:
PPMC INTERNATIONAL LIMITED
Item
A11: THE SITE/ EXISTING BUILDING
E | Site Boundaries
site boudaries are as shown in the project
| drawings |  | Item
F | Existing Buildings on or adjacent to the site
no existing building on site; existing
| department buildings adjacent to the site |  | Item
G | Existing mains/ Services
| Allow for relocating existing services |  | Item
Carried to Collection
A13: DESCRIPTION OF THE WORK
A | Elements of each new building
A 3- storey building block generally of
reinforced concrete foundations, columns,
| beams, floor slabs, cement sand mortar |  | Item
rendered sandcrete block walls, timber roof,
tile floor finish, painted walls with louvred windows
B | Dimensions and shape relating to
| each building (provided in project drawings) |  | Item
C | Heights between floors, (or refer to drawings) |  | Item
D | Total height, (or refer to drawings) |  | Item
A20: THE CONTRACT/ SUB-CONTRACT
Form of contract
Schedule of clause headings of standard
conditions
E | 1. Definitions |  | Item
F | 2. Interpretation |  | Item
G | 3. Language and law |  | Item
H | 4. Duties and authority of the Project
J | Manager |  | Item
K | 5. Delegation |  | Item
L | 6. Communications |  | Item
M | 7. Subcontracting |  | Item
N | 8. Other contractors |  | Item
P | 9. Personnel |  | Item
Q | 10. Employer's and contractor's risks |  | Item
R | 11. Employer's risks |  | Item
S | 12. Contractor's risks |  | Item
T | 13. Insurance |  | Item
U | 14. Site investigation reports |  | Item
V | 15. Queries about the contract data |  | Item
Carried to Collection
A | 16. Contractor to construct the works |  | Item
B | 17. The works to be completed by the
C | intended completion date |  | Item
D | 18. Approval by the Project Manager |  | Item
E | 19. Safety |  | Item
F | 20. Discoveries |  | Item
G | 21. Possession of the site |  | Item
H | 22. Access to the site |  | Item
J | 23. Instructions |  | Item
K | 24. Disputes |  | Item
L | 25. Procedure for Disputes |  | Item
M | 26. Replacement of Adjudicator |  | Item
N | 27. Programme |  | Item
P | 28. Extension of the Intended Completion Date |  | Item
Q | 29. Acceleration |  | Item
R | 30. Delays Ordered by the Project Manager |  | Item
S | 31. Management Meetings |  | Item
T | 32. Early Warning |  | Item
U | 33. Identifying Defects |  | Item
V | 34. Tests |  | Item
W | 35. Correction of Defects |  | Item
X | 36. Uncorrected Defects |  | Item
Y | 37. Bills of Quantities |  | Item
Z | 38. Changes in the Quantities |  | Item
AA | 39. Variations |  | Item
AB | 40. Payments for variations |  | Item
AC | 41. Cash Flow Forecasts |  | Item
AD | 42.Payment Certificates |  | Item
AE | 43. Payments |  | Item
AF | 44. Compensation Events |  | Item
AG | 45. Tax |  | Item
AH | 46. Currencies |  | Item
AJ | 47. Price Adjustment |  | Item
AK | 48. Retention |  | Item
AL | 49. Liquidated Damages |  | Item
AM | 50. Advance Payment |  | Item
AN | 51. Securities |  | Item
Carried to Collection
A | 52.Dayworks |  | Item
B | 53. Cost of Repairs |  | Item
C | 54. Completion |  | Item
D | 55. Taking Over |  | Item
E | 56. Final Account |  | Item
F | 57. Operating and Maintenance Manuals |  | Item
G | 58. Termination |  | Item
H | 59. Payment upon Termination |  | Item
J | 60. Property |  | Item
K | 61. Release from Performance |  | Item
L | Special condition or amendments to standard
| conditions |  | Item
M | Appendix insertions |  | Item
N | Employer's insurance responsibility (none) |  | Item
P | Performance guarantee bonds/ collatteral
| warrantees |  | Item
A30: EMPLOYER'S REQUIREMENTS: TENDERING
SUB-LETTING/ SUPPLY
Employer's requirement or limitations
Q | fixed charge |  | Item
R | time related charge |  | Item
A31: EMPLOYER'S REQUIREMENTS: PROVISION
CONTENT AND USE OF DOCUMENTS
Employer's requirement or limitations
S | fixed charge |  | Item
T | time related charge |  | Item
A32: EMPLOYER'S REQUIREMENTS:
MANAGEMENT OF THE WORKS
Employer's requirement or limitations
U | fixed charge |  | Item
V | time related charge |  | Item
Carried to Collection
A33: EMPLOYER'S REQUIREMENTS:
QUALITY STANDARDS/ CONTROL
Employer's requirement or limitations
A | fixed charge |  | Item
B | time related charge |  | Item
A34: EMPLOYER'S REQUIREMENT:
SECURITY/ SAFETY/ PROTECTION
Employer's requirements or limitations
Noise and pollution control
C | fixed charge |  | Item
D | time related charge |  | Item
Maintain adjoining buildings
E | fixed charge |  | Item
F | time related charge |  | Item
Maintain public and private roads
G | fixed charge |  | Item
H | time related charge |  | Item
Maintain live services
J | Fixed charge |  | item
K | Time related charge |  | item
Security
L | fixed charge |  | Item
M | time related charge |  | Item
Protection of work in all sections
N | fixed charge |  | Item
P | time related charge |  | Item
Carried to Collection
A36: EMPLOYER'S REQUIREMENT:
FACILITIES/ TEMPORARY WORKS/ SERVICES
Employer's requirements or limitations
Offices
A | fixed charge |  | Item
B | time related charge |  | Item
Sanitary accommodation
C | fixed charge |  | Item
D | time related charge |  | Item
Temporary fences, hoardings, screens and roofs
E | fixed charge |  | Item
F | time related charge |  | Item
Name boards
G | fixed charge |  | Item
H | time related charge |  | Item
Technical and surveying equipment
J | fixed charge |  | Item
K | time related charge |  | Item
Temperature and humidity
L | fixed charge |  | Item
M | time related charge |  | Item
Telephone/Facsimile installation and rental/
maintenance
N | fixed charge |  | Item
P | time related charge |  | Item
Others: Photographs
Q | fixed charge |  | Item
R | time related charge |  | Item
S | Telephone/Facsimile call charges |  | sum
Carried to Collection
A37: EMPLOYER'S REQUIREMENTS:
OPERATION/ MAINTENANCE OF THE
FINISHED BUILDING
Employer's requirements or limitations
A | fixed charge |  | Item
B | time related charge |  | Item
A40: CONTRACTOR'S GENERAL COST ITEMS:
MANAGEMENT AND STAFF
Management and staff
C | fixed charge |  | Item
D | time related charge |  | Item
A41: CONTRACTOR'S GENERAL COST ITEMS:
SITE ACCOMMODATION
Site accommodation
E | fixed charge |  | Item
F | time related charge |  | Item
A42: CONTRACTOR'S GENERAL COST ITEMS:
SERVICES AND FACILITIES
Services and facilities
Power
G | fixed charge |  | Item
H | time related charge |  | Item
Lighting
J | fixed charge |  | Item
K | time related charge |  | Item
Fuels
L | fixed charge |  | Item
M | time related charge |  | Item
Water
N | fixed charge |  | Item
P | time related charge |  | Item
Carried to Collection
Telephone and administration
A | fixed charge |  | Item
B | time related charge |  | Item
Safety, health and welfare
C | fixed charge |  | Item
D | time related charge |  | Item
Storage of materials
E | fixed charge |  | Item
F | time related charge |  | Item
Rubbish disposal
G | fixed charge |  | Item
H | time related charge |  | Item
Cleaning
J | fixed charge |  | Item
K | time related charge |  | Item
Drying out
L | fixed charge |  | Item
M | time related charge |  | Item
Protection of work I all sections
N | fixed charge |  | Item
P | time related charge |  | Item
Security
Q | fixed charge |  | Item
S | time related charge |  | Item
Maintain public and private roads
T | fixed charge |  | Item
U | time related charge |  | Item
Carried to Collection
Small plant and tools
A | fixed charge |  | Item
B | time related charge |  | Item
Others
C | fixed charge |  | Item
D | time related charge |  | Item
General attendance on nominated sub-contractor
E | fixed charge |  | Item
F | time related charge |  | Item
General attendance of nominated sub-contractors
in respect of the requirements
G | fixed charge |  | Item
H | time related charge |  | Item
A43: CONTRACTOR'S GENERAL COST ITEMS:
MECHANICAL PLANT
Hoists
J | fixed charge |  | Item
K | time related charge |  | Item
Personnel transport
L | fixed charge |  | Item
M | time related charge |  | Item
Transport
N | fixed charge |  | Item
P | time related charge |  | Item
Earthmoving plant
Q | fixed charge |  | Item
R | time related charge |  | Item
Concrete plant
S | fixed charge |  | Item
T | time related charge |  | Item
Carried to Collection
Paving and surfacing plant
A | fixed charge |  | Item
B | time related charge |  | Item
Others
C | fixed charge |  | Item
D | time related charge |  | Item
A44: CONTRACTOR'S GENERAL COST ITEMS:
TEMPORARY WORKS
Temporary roads
E | fixed charge |  | Item
F | time related charge |  | Item
Temporary walkways
G | fixed charge |  | Item
H | time related charge |  | Item
Access scaffolding
J | fixed charge |  | Item
K | time related charge |  | Item
Support scaffolding and propping
L | fixed charge |  | Item
M | time related charge |  | Item
Hoardings, fans, fencing, etc.
N | fixed charge |  | Item
P | time related charge |  | Item
Hardstanding
Q | fixed charge |  | Item
R | time related charge |  | Item
Traffic regulations
S | fixed charge |  | Item
T | time related charge |  | Item
Carried to Collection
Others
A | fixed charge |  | Item
B | time related charge |  | Item
A50: CONTRACTOR'S GENERAL COST ITEMS:
WORK/MATERIALS BY THE EMPLOYER
Work by others directly employed by the
Employer,
C | fixed charge |  | Item
D | time related charge |  | Item
Attendance on others directly employed by the
Employer,
E | fixed charge |  | Item
F | time related charge |  | Item
Materials provided by or on behalf of the
Employer,
G | fixed charge |  | Item
H | time related charge |  | Item
A51: NOMINATED SUB-CONTRACTORS
Sub-contrator's work
J | Description stated in accordance with
K | General Rule 10.3 |  | sum
L | Main contractor's profit |  | %
Special attendance,
Scaffolding
M | fixed charge |  | Item
N | time related charge |  | Item
Access roads
P | fixed charge |  | Item
Q | time related charge |  | Item
Carried to Collection
Hardstandings
A | fixed charge |  | Item
B | time related charge |  | Item
Positioning
C | fixed charge |  | Item
D | time related charge |  | Item
Storage
E | fixed charge |  | Item
F | time related charge |  | Item
Power
G | fixed charge |  | Item
H | time related charge |  | Item
Temperature and humidity
J | fixed charge |  | Item
K | time related charge |  | Item
Others
L | fixed charge |  | Item
M | time related charge |  | Item
A52: NOMINATED SUPPLIERS
N | Supplier's materials |  | sum
P | Main contractor's profit |  | %
Carried to Collection
A53: WORK BY STATUTORY AUTHORITIES/
UNDERTAKERS
A | Work by the local authority |  | sum
B | Work by statutory undertakers |  | sum
A54: PROVISIONAL WORK
C | Defined |  | sum
D | Undefined |  | sum
A55: DAYWORKS
E | Labour |  | sum
F | Materials |  | sum
G | Plant |  | sum
Carried to Collection
PRELIMINARIES COLLECTION
Page 1/1
Page 1/2
Page 1/3
Page 1/4
Page 1/5
Page 1/6
Page 1/7
Page 1/8
Page 1/9
Page 1/10
Page 1/11
Page 1/12
Page 1/13
| BILL No 1: PRELIMINARIES |  |  |  |  | 4556004.211
| CARRIED TO GRAND SUMMARY |  |  |  |  | 4556004 | 4556004.211

## Substructure
Item | Description | Qty | Unit | Rate | Amount
BILL No. 2: SUBSTRUCTURE
SUBSTRUCTURE ((All Provisional)
D: GROUNDWORK
D20: EXCAVATING AND FILLING
Site preparation
A | Remove trees; girth 600mm - 1.5m (Provisional) | 5 | Nr
B | Ditto;girth 1.50 - 3.00mm(Provisional) | 5 | Nr
C | Clearing site vegetation
| bushes, shrub, trees ≤ 600mm girth | 736 | m2
Excavating
D | Topsoil preservation
| Average depth 150mm | 2957 | m2
E | Trenches, Wall. Plinth beam, steps, tank, basement,
swimming pool
| Maximum depth ≤ 2.00m | 2794 | m3
F | Ditto; Maximum depth ≤ 4.00m | 858 | m3
G | Ditto; Maximum depth ≤ 6.00m |  | m3
H | Breaking out existing hard materials
| Extra over, rock excavation (Provisional) | 10 | m3
Excavated material
J | Off site | 579 | m3
Filling to excavation
K | Average thickness > 0.25m; arising from excavations,
| compacted in 300mm layers | 2074 | m3
L | Providing, laying, and compacting a layer of Rubble Soiling
| (75mm to 250mm sizes) to create a stable foundation base. | 368 | m3
M | Providing, laying and compacting layer of 20mm and
10mm aggregate placed directly beneath the concrete
| footing, or grade slab. | 245 | m3
N | Fine Tobacco Powder spreading up to 100mm thickness
below grade slab level with proper compaction and
| watering. | 184 | m2
C/F
B/F
Filling to excavation
| Average thickness > 0.25m; approved laterite obtained off | 645 | m3
A | site, compacted in 300mm layers
Surface treatment
B | Apply dieldrex anti-termite treatment chemical or
approved equal to excavated surfaces and foundations as
| directed | 123 | m2
E: IN SITU CONCRETE/ LARGE
PRE-CAST CONCRETE
E05: IN SITU CONCRETE CONSTRUCTING
GENERALLY
Mass in situ concrete: BS 5328, designed mix C15, 20mm
aggregate, minimum cement content 240 Kg/m3; vibrated
C | Blinding layer
| poured on earth | 9 | m3
Reinforced in situ concrete: BS 5328, designed mix C30, 20mm
aggregate, minimum cement content 240 Kg/m3; vibrated
D | Isolated foundations
| Reinforced | 645 | m3
E | Plinth Beam
| Isolated; reinforced | 330 | m3
F | Ground beams | 80 | m3
E20: FORMWORK FOR IN SITU CONCRETE
Wrought formwork, basic finish to
Isolated Foundations
G | plain vertical, height ≤ 150mm | 645 | m2
H | Plinth Beam
| plain vertical, height ≤ 250mm | 2276 | m2
J | Ground Beam | 491 | m2
E30: REINFORCEMENT FOR IN SITU CONCRETE
Reinforcement bars; BS 4449; hot rolled plain round high tensile
K | 25mm diameter in column | 0.92 | t
L | 20mm diameter in column | 2.55 | t
M | 16mm diameter in column | 0.13 | t
N | 8mm diameter as links in column | 0.99 | t
C/F
B/F
A | 32mm diameter in shear walls | 0.31 | t
B | 25mm diameter in shear walls | 0.41 | t
C | 20mm diameter in shear walls | 0.35 | t
D | 8mm diameter as links in shear walls | 0.13 | t
F: MASONRY
F10: BRICK/ BLOCK WALLING
Autoclaved aerated concrete (ACC) (35kg/cm²) in cement
and sand (1:6) mortar joint as described in:
E | 200mm thick wall; vertical | 26 | m2
J WATERPROOFING
J40: FLEXIBLE SHEET TANKING/ DAMP
PROOFING
F | Supply and lay approved 300 micron damp proof
polythene sheet on hardcore filling to receive concrete
| bed | 1406 | m2
SUB-STRUCTURE
Carried to Summary

## Ground Floor
Item | Description | Qty | Unit | Rate | Amount
BILL NO. 3 - GROUND FLOOR
E: IN SITU CONCRETE/ LARGE PRE-CAST CONCRETE
E05: IN SITU CONCRETE CONSTRUCTING
GENERALLY
Reinforced in situ concrete: BS 5328, designed mix C30, 20mm
aggregate, minimum cement content 240 Kg/m3; vibrated
A | Slabs reinforced, thickness ≤ 150mm | 140 | m3
B | Beams, reinforced | 125 | m3
C | Columns reinforced | 65 | m3
D | Staircases reinforced | 2 | m3
E | Shear Walls, reinforced | 35 | m3
Reinforced in situ concrete: BS 5328, designed mix C20, 20mm
aggregate, minimum cement content 240 Kg/m3; vibrated
F | Non-Structural wall, reinforced | 555 | m3
E20: FORMWORK FOR IN SITU CONCRETE
Wrought formwork, basic finish to
G | Soffits of slabs
slab thickness 200mm, horizontal, height to
| soffit 1.50 - 3.00m | 800 | m2
H | Beams
attached, rectangular
| cross-section, height to soffit 1.50 - 3.00m | 750 | m2
J | Columns
| regular shaped, | 413 | m2
K | Sides of Shear walls | 4163 | m2
L | Sides of Non-Structural wall | 263 | m2
E30: REINFORCEMENT FOR IN SITU CONCRETE
Reinforcement bars; BS 4449; hot rolled plain round high tensile
M | 25mm diameter in beams | 21.25 | t
N | 25mm diameter in columns | 13 | t
P | 16mm diameter in slab | 9.8 | t
Q | 25mm diameter in shear walls | 5.25 | t
R | 25mm diameter in Non-Structural Wall | 44.4 | t
IN SITU CONCRETE
Carried to Summary
F: MASONRY
F10: BRICK/ BLOCK WALLING
Autoclaved aerated concrete (ACC) (35kg/cm²) in cement
and sand (1:6) mortar joint as described in:
A | 200mm thick; vertical | 863 | m2
B | Ditto; 230mm thick | 284 | m2
C | Ditto; 250mm thick | 662 | m2
MASONRY
Carried to Summary
J: WATERPROOFING
J31 LIQUID APPLIED WATERPROOF ROOF COATINGS
D | Provide and applying cementitius crystalyn waterproofing
treatment by brush/spray application in 2 coats on RCC
slabs, walls, water tanks, lift pit, Etc. as per manufecturer's
| specification. | 49 | m2
E | Provide and applying cementitius crystalyn waterproofing
treatment by brush/spray application in 2 coats on RCC
slabs, walls, water tanks, lift pit, Etc. as per manufecturer's
| specification. | 46 | m2
APP menbrane 2 layers
F | Floors | 1225 | m2
WATERPROOFING
Carried to Summary
K: LININGS/ SHEATHING/ DRY
PARTITIONING
A | Providing and fixing suspended gypsum board false ceiling
using 12.5mm thick tapered edge gypsum plaster board
conforming to IS:2095, including G.I. perimeter channel of
0.5mm thick having 20mm x 27mm x 30mm, G.I.
intermediate channel 0.9mm thick 15mm x 45mm x 15mm
@ 1220mm c/c, and G.I. ceiling section 0.5mm thick
51.5mm x 26mm @ 457mm c/c, suspended from soffit
| with G.I. hanger @ 1220mm c/c. Complete as per drawing | 296 | m2
B | Providing and fixing suspended mineral fiber ceiling tile
system using 600mm x 600mm x 15/16mm thick tiles with
tegular/squared edge. Suspension system to comprise of
main runner 3600mm long @ 1200mm c/c, cross tee
1200mm @ 600mm c/c and 600mm cross tee @ 1200mm
c/c, with 25mm x 25mm wall angle at periphery. System
suspended from soffit with 4mm G.I. wire/rod hangers @
| 1200mm c/c. Complete as per manufacturer's specification | 118 | m2
C | Timber slat wall lining comprising 20 × 40 mm kiln-dried
hardwood slats fixed vertically at 20 mm clear spacing on
treated softwood battens with concealed stainless steel
screws, including all framing, grounds, trims, stop ends,
cutting, fitting, sanding and application of clear
| polyurethane finish, complete | 36 | m2
D | Marble wall lining comprising 20 mm thick polished
natural marble slabs, selected for uniform colour and
veining, fixed to prepared wall with approved proprietary
adhesive and stainless steel cramps/dowels where
required, including all cutting, drilling, jointing, edge
finishing, movement joints, sealant, making good, and
| cleaning on completion, complete | 27 | m2
LININGS/SHEATHING/DRY PARTITIONING
Carried to Summary
H: CLADDING/ COVERING
H10: PATENT GLAZING
A | External dry wall cladding with Travertine Stone, using dry
| cladding work with 22mm thick stone | 1471 | m2
B | Internal cladding with flexible sheets of traventine stone
| look. 4mm thickness and directly stick to the wall | 302 | m2
CLADDING/COVERING
Carried to Summary
L: WINDOWS/ DOORS/ STAIRS
L20: DOORS/SHUTTERS/HATCHES
DOORS
Wrought Walnut hardwood with trim moulding or approved equal in two panels as described
A | Hardwood framed single-leaf Solid Core panel door 900
| x2100x50mm (Finished), | 18 | Nr
B | Hardwood framed double-leaf panel door 1800
| x2400x50mm (Finished), | 4 | Nr
C | Hardwood framed single-leaf Solid Core panel door 750
| x2100x50mm (Finished), | 6 | Nr
D | Motorised Crash-rated Gate | 2 | Nr
E | Galvanised iron motorised rolling shutter | 1 | Nr
L30 STAIRS/ WALKWAYS/ BALUSTRADES
Blackcoated Balustrades primed and sprayed with anti-rust to specification
F | Glass balustrade with handrail (Stairs) as per drawings attached | 22 | m
L40: GENERAL GLAZING
G | Observation room glazed wall | 30 | m2
H | Ditto; glass partition | 107 | m2
WINDOWS/DOORS/STAIRS
Carried to Summary
M: SURFACE FINISHES
M10: CEMENT: SAND/ CONCRETE SCREEDS/
TOPPINGS
Heavy duty Concrete Screed, cement and sand (1:4) trowelled smooth
A | Floors
| 50mm thick, level and to falls only ≤ 150 | 885 | m2
Armoured Screed, steel fibre
Floors
B | 50mm thick, level and to falls only ≤ 150 | 11 | m2
M20: PLASTERED/ RENDERED/
ROUGHCAST COATINGS
Mortar, cement and sand (1:4, steel trowelled
Walls, External
C | width > 300mm, 12mm thick | 423 | m2
| Ditto; internal | 1019 | m2
D | Soffits of concrete ceiling
| width > 300mm, 10mm thick | 508 | m2
Wall Punning
E | Provide and apply 2 coats wall punning 8-12mm with
chicken mesh, using approved quality wall putty /
cement-based punning material over prepared wall
surfaces, including cleaning, surface preparation, curing,
and finishing smooth and even, complete in all respects as
| per specifications | 1337 | m2
M40: STONE/ CONCRETE/ QUARRY/ CERAMIC TILING/
MOSAIC
Ceramic tiles 300 x 600 x 6mm thick approved colour, two symmetrical joints layout, bedding in an approved adhesive;pointing with approved matching colour tile grout with on cement sand backing
F | Walls
| plain, width > 300mm | 127 | m2
Non-slip ceramic tiles 300 x 300 x 10mm thick approved colour,two symmetrical joints layout, bedding in an approved adhesive;pointing with approved matching colour tile grout with on cement sand backing
G | Floor
| plain, width > 300mm | 49 | m2
Carried Forward
Brought Forward
Porcelain Italian marble tiles 600 x 600 x 10mm thick approved colour,two symmetrical joints layout, bedding in an approved adhesive; pointing with approved matching colour tile grout with on cement sand backing
A | Floor
| plain, width > 300mm | 259 | m2
B | Skirting 100mm high | 254 | m
3mm Lab-grade epoxy resin (chemical-resistant)
C | Floor
| plain, width > 300mm | 520 | m2
Granite Flooring
D | Floor
| plain, width > 300mm | 17 | m2
Anti-Static rubber
E | Floor
| plain, width > 300mm | 51 | m2
M60: PAINTING/ CLEAR FINISHING
Prepare and Apply one coat primer and two coats of emulsion
paint as described to treated wall:
General surfaces rendered concrete and
block walls
F | girth > 300mm | 973 | m2
G | Soffits of concrete ceiling
| width > 300mm | 508 | m2
H | Ditto; false ceiling boards
| width > 300mm | 414 | m2
Prepare and Apply two coats of epoxy paint as described to
treated wall:
J | General surfaces rendered concrete and
block walls
| girth > 300mm | 412 | m2
Prepare and Apply two coats of weatherproof exterior paint
as described to treated wall:
General surfaces rendered concrete and
block walls
K | girth > 300mm | 963 | m2
SURFACE FINISHES
Carried to Summary
BILL NO. 3 - GROUND FLOOR
SUMMARY
IN SITU/ LARGE PRECAST CONCRETE
MASONRY
WATERPROOFING
LININGS/SHEATHING/DRY PARTITIONING
CLADDING/COVERING
WINDOWS/DOORS/STAIRS
SURFACE FINISHES
BILL No. 3 - GROUND FLOOR
CARRIED TO GENERAL SUMMARY

## 1st Floor
Item | Description | Qty | Unit | Rate | Amount
BILL NO. 3 - GROUND FLOOR
E: IN SITU CONCRETE/ LARGE PRE-CAST CONCRETE
E05: IN SITU CONCRETE CONSTRUCTING
GENERALLY
Reinforced in situ concrete: BS 5328, designed mix C30, 20mm
aggregate, minimum cement content 240 Kg/m3; vibrated
A | Slabs reinforced, thickness ≤ 150mm | 211 | m3
B | Beams, reinforced | 155 | m3
C | Columns reinforced | 50 | m3
D | Staircases reinforced | 2 | m3
E | Shear Walls, reinforced | 35 | m3
Reinforced in situ concrete: BS 5328, designed mix C20, 20mm
aggregate, minimum cement content 240 Kg/m3; vibrated
F | Non-Structural wall, reinforced | 210 | m3
E20: FORMWORK FOR IN SITU CONCRETE
Wrought formwork, basic finish to
G | Soffits of slabs
slab thickness 200mm, horizontal, height to
| soffit 1.50 - 3.00m | 1200 | m2
H | Beams
attached, rectangular
| cross-section, height to soffit 1.50 - 3.00m | 930 | m2
J | Columns
| regular shaped, | 318 | m2
K | Sides of Shear walls | 263 | m2
L | Sides of Non-Structural wall | 1575 | m2
E30: REINFORCEMENT FOR IN SITU CONCRETE
Reinforcement bars; BS 4449; hot rolled plain round high tensile
M | 25mm diameter in beams | 26.35 | t
N | 25mm diameter in columns | 10 | t
P | 16mm diameter in slab | 14.7 | t
Q | 25mm diameter in shear walls | 5.25 | t
R | 25mm diameter in Non-Structural Wall | 16.8 | t
IN SITU CONCRETE
Carried to Summary
F: MASONRY
F10: BRICK/ BLOCK WALLING
Autoclaved aerated concrete (ACC) (35kg/cm²) in cement
and sand (1:6) mortar joint as described in:
A | 200mm thick; vertical | 589 | m2
B | Ditto; 250mm thick | 574 | m2
MASONRY
Carried to Summary
J31 LIQUID APPLIED WATERPROOF ROOF COATINGS
Provide and applying cementitius crystalyn waterproofing
treatment by brush/spray aoolication in 2 coats on RCC
slabs, walls, water tanks, lift pit, Etc. as per manufecturer's
specification.
C | RCC Slabs, walls, water tanks, lift pit
| width > 300mm | 64 | m2
D | APP Membrane, 2 layers on roof | 1350 | m2
WATERPROOFING
Carried to Summary
K: LININGS/ SHEATHING/ DRY
PARTITIONING
A | Providing and fixing suspended gypsum board false ceiling
using 12.5mm thick tapered edge gypsum plaster board
conforming to IS:2095, including G.I. perimeter channel of
0.5mm thick having 20mm x 27mm x 30mm, G.I.
intermediate channel 0.9mm thick 15mm x 45mm x 15mm
@ 1220mm c/c, and G.I. ceiling section 0.5mm thick
51.5mm x 26mm @ 457mm c/c, suspended from soffit
| with G.I. hanger @ 1220mm c/c. Complete as per drawing | 291 | m2
B | Providing and fixing suspended mineral fiber ceiling tile
system using 600mm x 600mm x 15/16mm thick tiles with
tegular/squared edge. Suspension system to comprise of
main runner 3600mm long @ 1200mm c/c, cross tee
1200mm @ 600mm c/c and 600mm cross tee @ 1200mm
c/c, with 25mm x 25mm wall angle at periphery. System
suspended from soffit with 4mm G.I. wire/rod hangers @
| 1200mm c/c. Complete as per manufacturer's specification | 140 | m2
C | Providing and fixing suspended acoustic gypsum board
false ceiling using 12.5mm thick perforated gypsum board
with regular/random perforation, laminated with acoustic
tissue on back side, fixed to G.I. grid system. Grid to
comprise perimeter channel 20x27 x30mm, intermediate
channel 15x45x15mm @ 600mm c/c, ceiling section
51.5x26mm @ 300mm c/c, suspended with G.I. hangers @
900mm c/c. Rate to include 50mm thick glass
wool/rockwool insulation of 32-48 kg/m³ density over the
| board. Complete with jointing, finishing ready for paint | 51 | m2
D | Providing and fixing suspended Grid Type false ceiling
using 12.5mm thick tapered edge gypsum board textured
Finish sheet, including G.I. perimeter channel of 0.5mm
thick having 20mm x 27mm x 30mm, G.I. intermediate
channel 0.9mm thick 15mm x 45mm x 15mm @ 1220mm
c/c, and G.I. ceiling section 0.5mm thick 51.5mm x 26mm
@ 457mm c/c, suspended from soffit with G.I. hanger @
| 1220mm c/c. Complete as per drawing | 65 | m2
E | Acoustic wall lining comprising 25 mm thick fabric-faced
sound-absorbing panels with high-density mineral wool
core, mounted on moisture-resistant MDF backing and fixed
to wall with concealed proprietary clips/adhesive,
including all perimeter trims, corner details cutting and
fitting around openings, complete in accordance with the
| manufacturer's recommendations. | 58 | m2
C/F
B/F
A | Timber slat wall lining comprising 20 × 40 mm kiln-dried
hardwood slats fixed vertically at 20 mm clear spacing on
treated softwood battens with concealed stainless steel
screws, including all framing, grounds, trims, stop ends,
cutting, fitting, sanding and application of clear
| polyurethane finish, complete | 21 | m2
LININGS/SHEATHING/DRY PARTITIONING
Carried to Summary
L: WINDOWS/ DOORS/ STAIRS
L10: WINDOWS/ ROOFLIGHTS/ SCREENS/ LOUVRES
Aluminum framed window, as specified in ANNEXURE 2: "8mm + 8mm + 16 (ARGON GAP) DGU GLAZING". Comprising thermally broken powder-coated aluminum frame (extruded sections conforming to IS:733 and IS:1285), 8mm + 16mm Argon gas gap + 8mm Double Glazed Unit (DGU), low-E coating (hard coat) to inner face of outer pane, Argon gas fill (90% concentration), warm edge spacer bar (stainless steel or silicone foam), push-bar opening mechanism, SS304 friction stays (2 pairs), and EPDM perimeter seals. Fixed to structural opening with stainless steel anchors at 450mm centers. All glazing, sealants, and fixings included. Assumption: 1 window type W-01 on FF (as per schedule). Measured by area as exceeds 3.00 m².
A | Window type W-01 (L30:1 – Window exceeding 3.00 m²) – Top-hung aluminum framed window, 3160mm wide × 1200mm high (3.79 m²). | 4 | m2
B | Window type W-05 (L30:1 – Window exceeding 3.00 m²) – Vertical sliding aluminum framed window, 1200mm wide × 7800mm high (9.36 m²). Spanning from LVL +3900 to LVL +11400 (double height – GF to FF) | 10 | m2
Window type – Fixed ribbon window / curtain walling, comprising thermally broken powder-coated aluminum framing system (mullions at maximum 1500mm centers, transoms at 1200mm centers), 8mm + 16mm Argon gap + 8mm DGU throughout, low-E coating, structural silicone glazing, SS304 fixings, and EPDM gaskets. Non-opening. All framing, glass, sealants, and fixings included. Assumption: 1 window type W-02 on FF. Sill at 2100 B.BOTTOM as per schedule.
C | Window type W-02 – 13940mm wide × 1200mm high (16.73 m²) | 17 | m2
D | Window type W-03 – 450mm wide × 1200mm high (22.14 m²). Specification as W-02. All framing, glass, sealants, and fixings included. Assumption: 1 window type W-03 on FF. Sill at 2100 B.BOTTOM. | 22 | m2
E | Window type W-04 12600mm wide × 1200mm high (15.12 m²). Specification as W-02. All framing, glass, sealants, and fixings included. Assumption: 1 window type W-04 on FF. Sill at 2100 B.BOTTOM. | 15 | m2
C/F
B/F
L20: DOORS/SHUTTERS/HATCHES
DOORS
Wrought Walnut hardwood with trim moulding or approved equal in two panels as described
A | Hardwood framed single-leaf Solid Core panel door 900
| x2100x50mm (Finished), | 10 | Nr
Supply and fixed glazed door as described below:
B | Double glazed frameless door 1200 x 2400mm | 2 | Nr
C | Glass partition door 900 x 2400mm | 1 | Nr
L40: GENERAL GLAZING
D | Glass partition | 64 | m2
WINDOWS/DOORS/STAIRS
Carried to Summary
M: SURFACE FINISHES
M10: CEMENT: SAND/ CONCRETE SCREEDS/
TOPPINGS
Heavy duty Concrete Screed, cement and sand (1:4) trowelled smooth
A | Floors
| 50mm thick, level and to falls only ≤ 150 | 525 | m2
M20: PLASTERED/ RENDERED/
ROUGHCAST COATINGS
Mortar, cement and sand (1:3, steel trowelled
Walls, external
B | width > 300mm, 12mm thick | 1127 | m2
C | Ditto; internal | 1264 | m2
Wall Punning
D | Provide and apply 2 coats wall punning 8-12mm with
chicken mesh, using approved quality wall putty /
cement-based punning material over prepared wall
surfaces, including cleaning, surface preparation, curing,
and finishing smooth and even, complete in all respects as
| per specifications | 1161 | m2
M40: STONE/ CONCRETE/ QUARRY/ CERAMIC TILING/
MOSAIC
Ceramic tiles 300 x 600 x 6mm thick approved colour, two symmetrical joints layout, bedding in an approved adhesive;pointing with approved matching colour tile grout with on cement sand backing
E | Walls
| plain, width > 300mm | 170 | m2
Porcelain Italian marble tiles 600 x 600 x 10mm thick approved colour,two symmetrical joints layout, bedding in an approved adhesive; pointing with approved matching colour tile grout with on cement sand backing
F | Floor
| plain, width > 300mm | 129 | m2
G | Ditto; 1600 x 800mm | 191 | m2
Ceramic tiles 600 x 600 x 10mm thick approved colour,two symmetrical joints layout, bedding in an approved adhesive; pointing with approved matching colour tile grout with on cement sand backing
H | Floor
| plain, width > 300mm | 153 | m2
D | Skirting 100mm High | 254 | m
C/F
B/F
Carpet tile 600 x 600mm
A | Floor
| plain, width > 300mm | 166 | m2
M60: PAINTING/ CLEAR FINISHING
Prepare and Apply one coat primer and two coats of emulsion
paint as described to treated wall:
General surfaces rendered concrete and
block walls
B | girth > 300mm | 348 | m2
Ditto; false ceiling boards
C | width > 300mm | 525 | m2
SURFACE FINISHES
Carried to Summary
BILL NO. 3 - FIRST FLOOR
SUMMARY
IN SITU/ LARGE PRECAST CONCRETE
MASONRY
WATERPROOFING
LININGS/SHEATHING/DRY PARTITIONING
WINDOWS/DOORS/STAIRS
SURFACE FINISHES
BILL No. 3 - FIRST FLOOR
CARRIED TO GENERAL SUMMARY

## 2nd Floor
Item | Description | Qty | Unit | Rate | Amount
BILL No. 4 - SECOND FLOOR
E: IN SITU CONCRETE/ LARGE
PRE-CAST CONCRETE
E05: IN SITU CONCRETE CONSTRUCTING
GENERALLY
Reinforced in situ concrete: BS 5328, designed mix C30, 20mm
aggregate, minimum cement content 240 Kg/m3; vibrated
A | Slabs reinforced, thickness ≤ 150mm | 211 | m3
B | Beams, reinforced | 155 | m3
C | Columns reinforced | 45 | m3
D | Shear Walls, reinforced | 35 | m3
Reinforced in situ concrete: BS 5328, designed mix C20, 20mm
aggregate, minimum cement content 240 Kg/m3; vibrated
E | Non-Structural wall, reinforced | 210 | m3
E20: FORMWORK FOR IN SITU CONCRETE
Wrought formwork, basic finish to
F | Soffits of slabs
slab thickness 200mm, horizontal, height to
| soffit 1.50 - 3.00m | 1200 | m2
G | Beams
attached, rectangular
| cross-section, height to soffit 1.50 - 3.00m | 930 | m2
H | Columns
| regular shaped, | 286 | m2
J | Sides of Shear walls | 263 | m2
K | Sides of Non-Structural wall | 1575 | m2
E30: REINFORCEMENT FOR IN SITU
CONCRETE
Reinforcement bars; BS 4449; hot rolled plain round high tensile
L | 25mm diameter in beams | 23.25 | t
M | 25mm diameter in columns | 9 | t
N | 16mm diameter in slab | 14.7 | t
P | 25mm diameter in shear walls | 5.25 | t
Q | 25mm diameter in Non-Structural Wall | 16.8 | t
IN SITU CONCRETE
Carried to Summary
F: MASONRY
F10: BRICK/ BLOCK WALLING
Autoclaved aerated concrete (ACC) (35kg/cm²) in cement
and sand (1:6) mortar joint as described in:
A | 200mm thick; vertical | 412 | m2
B | Ditto; 250mm thick | 402 | m2
MASONRY
Carried to Summary
J: WATERPROOFING
J31 LIQUID APPLIED WATERPROOF ROOF COATINGS
APP Membrane 2 layers
C | Roof
| width > 300mm | 1225 | m2
D | Terrace MS roof waterproofing : Provide and laying APP
modified polymeric bituminious membrane 3mm thick,
reinforced with non woven polyster mat, with mineral
finish on top surface membrane to be torch applied with
100 mm side laps and 150 mm end laps, fully bonded to
| substrate | 1225 | m2
WATERPROOFING
Carried to Summary
L: WINDOWS/ DOORS/ STAIRS
L: WINDOWS/ DOORS/ STAIRS
L10: WINDOWS/ ROOFLIGHTS/ SCREENS/ LOUVRES
Windows and window frames,
Curtain Wall
A | Curtain wall as specified, overall dimensions 9000mm x
| 8400mm DGU | 76 | m2
Supply and fix strip window as specified:
B | Strip window 1500mm high | 80 | m2
C | Window type W-06 (L30:4 – Curtain walling / Ribbon window) – Fixed ribbon window / curtain walling, 15450mm wide × 1800mm high (27.81 m²). Comprising thermally broken powder-coated aluminum framing system (mullions at maximum 1500mm centers, transoms at 1800mm centers), 8mm + 16mm Argon gap + 8mm DGU throughout, low-E coating, structural silicone glazing, SS304 fixings, and EPDM gaskets. Non-opening. All framing, glass, sealants, and fixings included. Assumption: 1 window type W-06 on SF (from schedule). Sill at 1500 B.BOTTOM. | 28 | m2
D | Window type W-07 (L30:4 – Curtain walling / Ribbon window) – Fixed ribbon window / curtain walling, 36100mm wide × 1800mm high (64.98 m²). Comprising thermally broken powder-coated aluminum framing system (mullions at maximum 1500mm centers, transoms at 1800mm centers), 8mm + 16mm Argon gap + 8mm DGU throughout, low-E coating, structural silicone glazing, SS304 fixings, and EPDM gaskets. Non-opening. All framing, glass, sealants, and fixings included. Assumption: 1 window type W-07 on SF (from your schedule). Sill at 1500 B.BOTTOM. | 65 | m2
E | Window type W-08 (L30:4 – Curtain walling / Ribbon window) – Fixed ribbon window / curtain walling, 28300mm wide × 1800mm high (50.94 m²). Specification as W-07. All framing, glass, sealants, and fixings included. Assumption: 1 window type W-08 on SF (from your schedule). Sill at 1500 B.BOTTOM. | 51 | m2
F | Window type W-09 (L30:4 – Curtain walling / Ribbon window) – Fixed ribbon window / curtain walling, 12600mm wide × 1800mm high (22.68 m²). Specification as W-07. All framing, glass, sealants, and fixings included. Assumption: 1 window type W-09 on SF (from your schedule). Sill at 1500 B.BOTTOM. | 23 | m2
C/F
B/F
A | Window type W-10 (L30:1 – Window exceeding 3.00 m²) – Top-hung aluminum framed window, 8800mm wide × 900mm high (7.92 m²). Comprising thermally broken powder-coated aluminum frame, 8mm + 16mm Argon gap + 8mm DGU, low-E coating, push-bar opening mechanism (multiple sections), SS304 friction stays at maximum 600mm centers, and EPDM perimeter seals. Assumption: 1 window type W-10 on SF (from your schedule). Sill at 2400 B.BOTTOM. | 8 | m2
B | Window type W-11 (L30:6 – Windows 3.00 m² or less) – Top-hung aluminum framed window, 1200mm wide × 1800mm high (2.16 m² – measured as numbered unit). Comprising thermally broken powder-coated aluminum frame, 8mm + 16mm Argon gap + 8mm DGU, low-E coating, push-bar opening mechanism, SS304 friction stays, and EPDM perimeter seals. Assumption: 1 window type W-11 on SF (from your schedule). Sill at 1500 B.BOTTOM. Measured as numbered unit as area does not exceed 3.00 m². | 1 | No.
L20: DOORS/SHUTTERS/HATCHES
DOORS
Wrought Walnut hardwood with trim moulding or approved equal in two panels as described
C | Hardwood framed single-leaf Solid Core panel door 900
| x2100x50mm (Finished), | 2 | Nr
Supply and fixed glazed door as described below:
D | Main entry auto-sliding glass door 3600 x 2700mm | 1 | Nr
E | Glazed door 1200 x 2400mm | 2 | Nr
F | Glazed door 1200 x 2100mm | 4 | Nr
Vault Door
G | high Security armoured door 1200 x 2100mm | 1 | Nr
L40: GENERAL GLAZING
H | Special glass as observation room glazed wall 8,450mm x | 30 | m2
1,800mm both sides
WINDOWS/DOORS/STAIRS
Carried to Summary
M: SURFACE FINISHES
M10: CEMENT: SAND/ CONCRETE SCREEDS/
TOPPINGS
Heavy duty Concrete Screed, cement and sand (1:4) trowelled smooth
A | Floors
| 50mm thick, level and to falls only ≤ 150 | 1225 | m2
M20: PLASTERED/ RENDERED/ ROUGHCAST COATINGS
Mortar, cement and sand (1:3, steel trowelled
Walls, External
B | width > 300mm, 12mm thick | 1168 | m2
SURFACE FINISHES
Carried to Summary
BILL No. 4: FIRST FLOOR
SUMMARY
IN SITU/ LARGE PRECAST CONCRETE
MASONRY
WATERPROOFING
WINDOWS/DOORS/STAIRS
SURFACE FINISHES
BILL No. 4 - SECOND FLOOR
CARRIED TO GENERAL SUMMARY

## Electric Work_BOQ
GOLDBOD NATIONAL ASSAY CENTER
ELECTRIC WORKS
Item | Description | Unit | Qty | Rate | Amount
A | Point Wiring Point wiring for Light / Bell with 2-1.5 sq.mm & earth wire of 1.5 sq.mm (Green) both are of ISI marked 1.1 KV grade FRLS PVC insulated multi strand copper wires up to 10 mtr length , in below type of pipe erected with 6A Modular type switch / bell push & accessories and earth continuity of following type, erected on PVC / Metallic/Wooden box, single mounting base frame covered with textured/metallic/white front plate modules erected on / in wall / ceiling as per pipe erected, with necessary Lamp holder/ceiling rose / H.D.Connector as directed. (f) with medium class Rigid PVC pipe and accessories erected concealed in wall/ceiling complete. Cat. III | No.
B | Point wiring for Tissino / Modular secondary light point with 2-1.5 sq.mm & earth wire of 1.5 sq.mm (green) both are of ISI marked 1.1 KV grade FRLS PVC insulated multi strand copper wires, in below type of pipe to be erected complete with earth continuity and necessary connection with primary light with accessories erected on Metal / PVC / wooden box covered with 3 mm thick PC(Polycarbonate) / Acrylic sheet for open / concealed wiring. with necessary Lamp holder / ceiling rose / H.D.Connector as directed. Note:- Maximum up to 6 mtrs length, excess will be considered as Mains for Secondary Point (f) with medium class Rigid PVC pipe and accessories erected concealed in wall/ceiling complete | No
C | Point wiring for Two Way Controlled Light Point with 2-1.5 sq.mm & earth wire of 1.5 sq.mm (green) both are of ISI marked 1.1 KV grade FRLS PVC insulated multi strand copper wires up to 10 mtr length, in following type of pipe to be erected concealed in / flushed on wall / ceiling complete with 6A Tissino Type ISI marked accessories with earth continuity erected on Metal/PVC//Wooden box covered with 3 mm thick PC(Polycarbonate) / Acrylic sheet. with necessary Lamp holder/ceiling rose / H.D.Connector as directed. (f) with medium class Rigid PVC pipe and accessories erected concealed in wall/ceiling complete | No.
D | Point wiring for FAN with 2-1.5 sq.mm & earth wire of 1.5 sq.mm (Green) both are of .ISI marked 1.1 KV Grade FRLS PVC insulated multi strand copper wires up to 10 mtr length, in below type of pipe erected with 6A Modular type switch and hum free EME step type electronic fan regulator mounted and accessories with earth continuity of following type erected on PVC / Metallic/Wooden box, single mounting base frame covered with textured/metallic/white front plate modules erected on / in wall / ceiling as per pipe erected. with necessary ceiling rose / H.D.Connector as directed. (f) with medium class Rigid PVC pipe and accessories erected concealed in wall/ceiling complete.Cat.III | No.
E | Point wiring for on board Looped Plug with 6A Modular type switch & 5 pin socket erected on PVC / Metallic/Wooden box, single mounting base frame covered with textured / metallic/white front plate modules erected on / in wall / ceiling with following type accessories.Cat. III | No.
F | Point wiring for Individual Plug with & earth wire of 1.5 sq.mm (Green) both are of ISI marked 1.1 KV grade FRLS PVC insulated multi strand copper wires up to 10 mtr length, in below type of pipe erected complete with Modular type switch & 5 pin Plug erected on PVC / Metallic/Wooden box covered with appropriate front plate modules erected on / in wall / ceiling as per pipe erected with following type of accessories. [I] For 6A Plug and 6 a switch with 2-1.5 sq.mm Cu. Wire from nearby switchboard/mcb db board (f) with medium class Rigid PVC pipe and accessories erected concealed in wall/ceiling complete.Cat.III | No.
G | Point wiring for Individual Plug with & earth wire of 1.5 sq.mm (Green) both are of ISI marked 1.1 KV grade FRLS PVC insulated multi strand copper wires up to 10 mtr length, in below type of pipe erected complete with Modular type switch & 5 pin Plug erected on PVC / Metallic/Wooden box covered with appropriate front plate modules erected on / in wall / ceiling as per pipe erected with following type of accessories. [II] For 16A Plug and 16 amp switch with 2-2.5 sq.mm Cu. Wire from mcb db board. (f) with medium class Rigid PVC pipe and accessories erected concealed in wall/ceiling complete. Cat. III | No.
C/F
B/F
A | Point wiring for Individual Plug with & earth wire of 1.5 sq.mm (Green) both are of ISI marked 1.1 KV grade FRLS PVC insulated multi strand copper wires up to 10 mtr length, in below type of pipe erected complete with Modular type switch & 5 pin Plug erected on PVC / Metallic/Wooden box covered with appropriate front plate modules erected on / in wall / ceiling as per pipe erected with following type of accessories. [III] For 16A Plug and 16 amp switch with 2-4 sq.mm Cu. Wire with 2.5 sq.mm ( green) earthing wire from mcb d b board. (f) with medium class Rigid PVC pipe and accessories erected concealed in wall/ceiling complete | No.
B | Providing & erecting Switch board for Computer or electric apparatus consisting of following modular type accessories mounted with PVC / Metallic concealed/open box with single mounting base frame covered with textured/metallic /white front plate,modules erected with necessary connections as directed 1 no. 6A/16A universal plug-switch combined. 3 nos. 6A Switch 3 nos. 6A 5 pin Plug For Modular Type Accessories. Cat. III | No.
C | Providing and erecting ISI mark Medium class RIGID PVC PIPES of following size complete to be erected on/in wall or ceiling erected with necessary PVC fittings & Junction boxes fixed with adhesive solution & Clamps with following dia of pipes, in approved manner as directed (b) 25 mm | m
D | Providing and erecting ISI mark Medium class RIGID PVC PIPES of following size complete to be erected on/in wall or ceiling erected with necessary PVC fittings & Junction boxes fixed with adhesive solution & Clamps with following dia of pipes, in approved manner as directed (c) 32 mm | m
E | Providing and erecting ISI mark Medium class RIGID PVC PIPES of following size complete to be erected on/in wall or ceiling erected with necessary PVC fittings & Junction boxes fixed with adhesive solution & Clamps with following dia of pipes, in approved manner as directed (d) 40 mm | m
F | Raceway & Junction Box SITC of Under floor pregalvanized junction box with knock outs suitable for 60x25mm and 90x35mm three PVC duct entries in all the four sides. The box is suitable for 70mmscreed height with a powder coated trap and frame (2+3mm) suitable for Marble flooring with 10mm recess, height adjustable. Dimensions:400 x 400 x 65-90mm | No.
G | SITC of Under floor pregalvanized junction box with knock outs suitable for 60x25mm and 90x35mm two PVC duct entries in all the four sides. The box is suitable for 70mm screed height with a powder coated trap and frame (2+3mm) suitable for Marble flooring with 10mm recess. height adjustable. Dimensions:300 x 300 x 65-90mm | No.
H | SITC of Under floor pregalvanized junction box with knock outs suitable for 60x25mm / 90x35mm single PVC duct entry in all the four sides. The box is suitable for 70mm screed height with a powder coated trap and frame (2+3mm) suitable for Marble flooring with 20mm recess. height adjustable. Dimensions:225 x 225 x 65-90mm | No.
J | SITC of Under floor pregalvanized junction box with knock outs suitable for 60x25mm / 90x35mm single PVC duct entry in all the four sides. The box is suitable for 70mm screed height with a powder coated trap and frame (2+3mm) suitable for Marble flooring with 20mm recess. height adjustable. Dimensions:150 x 150 x 65-90mm | No.
K | SITC of 50 mm x 38 mm x 1 compatment high impact PVC material (hammer test according to DIN EN 60068-2-75) in compliance with the relevant standard to EN 50085-2-2 floor Trunking as per specification with all fixing accessories | m
L | SITC of 100 mm x 38 mm x 2 compartment high impact PVC material (hammer test according to DIN EN 60068-2-75) in compliance with the relevant standard to EN 50085-2-2 floor Trunking as per specification with all fixing accessories | m
M | SITC of 150 mm x 38 mm x 3 compartment high impact PVC material (hammer test according to DIN EN 60068-2-75) in compliance with the relevant standard to EN 50085-2-2 floor Trunking as per specification with all fixing accessories | m
C/F
B/F
A | SITC of 225 mm x 38 mm x 3 compartment high impact PVC material (hammer test according to DIN EN 60068-2-75) in compliance with the relevant standard to EN 50085-2-2 floor Trunking as per specification with all fixing accessories | m
B | SITC of 300 mm x 38 mm x 3 compartment high impact PVC material (hammer test according to DIN EN 60068-2-75) in compliance with the relevant standard to EN 50085-2-2 floor Trunking as per specification with all fixing accessories | m
C | SITC of Vertical connection box made of galvanised sheet steel for feeding the cables from the Distribution Box through the under floor ducts suitable for 225 mm width UPVC ducts as per specification & drawing of with all fixing accessories | No.
D | SITC of Vertical connection box made of galvanised sheet steel for feeding the cables from the Distribution Box through the under floor ducts suitable for 300 mm width UPVC ducts as per specification & drawing of with all fixing accessories | No.
E | MAINS : ( not for Point wiring ) Mains with ISI marked, 1.5KV grade electrolyte multi stranded, annealed copper conductor with heat resistant PVC insulated conforms to IS 694, IEC - 227 erected in existing pipe of following size (Specifically for control panel, relays, power switchgears, motor starters & control wiring) with required size of copper lugs, nuts and bolts if required. Supplying and Laying of 4 nos. of 10 sq mm Cu. FRLS flexible wires with 2 nos 4 sqmm Cu. FRLS flexible wires | m
F | Mains with 1.1 KV grade FRLS PVC insulated ISI marked stranded Copper conductor wire in following type of pipe to be erected in / on wall / ceiling with 2.5 sq. mm copper conductor FRLS PVC insulated stranded wire of green colour for earth continuity of following size Supplying and Laying of 4 nos. of 6 sq mm Cu. FRLS flexible wires with 2 nos 2.5 sqmm Cu. FRLS flexible wires | m
G | Mains with 1.1 KV grade FRLS PVC insulated ISI marked stranded Copper conductor wire in following type of pipe to be erected in / on wall / ceiling with 2.5 sq. mm copper conductor FRLS PVC insulated stranded wire of green colour for earth continuity of following size Supplying and Laying of 4 nos. of 4 sq mm Cu. FRLS flexible wires with 2 nos 2.5 sqmm Cu. FRLS flexible wires | m
H | Mains with 1.1 KV grade FRLS PVC insulated ISI marked stranded Copper conductor wire in following type of pipe to be erected in / on wall / ceiling with 2.5 sq. mm copper conductor FRLS PVC insulated stranded wire of green colour for earth continuity of following size Supplying and Laying of 2 nos. of 6 sq mm Cu. FRLS flexible wires with 1 nos 2.5 sqmm Cu. FRLS flexible wires | m
J | Mains with 1.1 KV grade FRLS PVC insulated ISI marked stranded Copper conductor wire in following type of pipe to be erected in / on wall / ceiling with 2.5 sq. mm copper conductor FRLS PVC insulated stranded wire of green colour for earth continuity of following size Supplying and Laying of 2 nos. of 4 sq mm Cu. FRLS flexible wires with 1 nos 2.5 sqmm Cu. FRLS flexible wires | m
K | Mains with 1.1 KV grade FRLS PVC insulated ISI marked stranded Copper conductor wire in following type of pipe to be erected concealed in /flushed on wall/ceiling, with 1.5 sq. mm copper conductor FRLS PVC insulated stranded wire of green colour for earth continuity of following size Supplying and Laying of 2 nos. of 2.5 sq mm Cu. FRLS flexible wires with 1 nos 1.5 sqmm Cu. FRLS flexible wires | m
c/f
b/f
A | Distribution Board Supply, Assembling, grouting, leveling Connecting & testing D.B of IP 43 of specified make. Distribution Board-VTPN Supply, Erecting, testing and commissioning of only VTPN D.B. PPI type with space for FPMCB as incoming and space for DPELMCB and 4 TPMCB as outgoing per phase (i.e. 4 way VTPN D.B.) | No.
B | Distribution Board-TPN Supply, Erecting, testing and commissioning of only TPN D.B. PPI type with space for FPMCB as incoming and space for DPELMCB and 8 SPMCB as outgoing per phase (i.e. 12 way per phase D.B.) | No.
C | Supply, Erecting, testing and commissioning of only TPN D.B. PPI type with space for FPMCB as incoming and space for DPELMCB and 4 SPMCB as outgoing per phase (i.e. 8 way per phase D.B.) | No.
D | Distribution Board-SPN Supply, Erecting, testing and commissioning of SPN D.B. with space for DPELMCB as incoming and 8 SPMCB as outgoing per phase (i.e. 12 way D.B.) | No.
E | Supply, Erecting, testing and commissioning of SPN D.B. with space for DPELMCB as incoming and 4 SPMCB as outgoing per phase (i.e. 8 way D.B.) | No.
F | MCB providing and erecting Miniature circuit breaker single pole 0.5A to 2A system and having breaking capacity 10 KA to be erected in existing box. confirming to IS 8828/1996 with ISI Mark | No.
G | Miniature circuit breaker single pole suitable to operate on 240 V A.C. system and having breaking capacity 10 KA to be erected in existing box. confirming to IS 8828/1996 with ISI Mark 6 to 25 A SP MCB | No.
H | 40Amp SP MCB | No.
J | Providing & erecting 240 V MCB double pole switch for motor & inductive load (C Curve) having 10 KA breaking capacity & confirms to IS : 8828 in existing box having following capacity 6 to 32 A DP MCB | No.
K | 40 A DP MCB | No.
L | Approved make ELCBs / RCCBs conforming to IS: 12640 and having sensitivity of 30 mA and Short Circuit withstand capacity of 6 KA and suitable for operation on single phase 240 V. having characteristic of quick action & tripping with all advance feature & do not incorporate any electronic component. for following Max. rating erected as directed 25 to 32A / 30mA DP ELMCB | No.
M | 40 A / 30 mA DP ELMCB | No.
N | 63 A / 30 mA DP ELMCB | No.
P | Providing & erecting 415 V MCB three Pole for Motor & Inductive Load (C Curve) having 10KA breaking capacity & confirms to IS :8828 in existing box having following capacity (a) 6 to 32 Amp. Cat.III | No.
C/F
B/F
A | Providing & erecting 415 V MCB three Pole for Motor & Inductive Load (C Curve) having 10KA breaking capacity & confirms to IS :8828 in existing box having following capacity (b) 40 Amp. Cat.III | No.
B | Providing & erecting 415 V MCB Four Pole for Motor & Inductive Load (C Curve) having 10KA breaking capacity & confirms to IS :8828 in existing box having following capacity 6 to 32A FP MCB | No.
C | 40 A FP MCB | No.
D | 63 A FP MCB | No.
E | Approved make four pole moulded case circuit breaker having breaking Capacity ICU of 35KA. At 415 V, having normal current rating up to 125A. With fixed thermal & magnetic release suitable to work on A.C. supply 50 c/s. with all iternal connections & complete erected in existing 16 G.M.S. housing. ICS= 100% of ICU only. | No.
F | Approved make four pole moulded case circuit breaker having breaking Capacity ICU of 35KA. At 415 V, having normal current rating up to 200A. With fixed thermal & magnetic release suitable to work on A.C. supply 50 c/s. with all iternal connections & complete erected in existing 16 G.M.S. housing. ICS= 100% of ICU only. | No.
G | Supplying & erecting approved make Digital time switch having lithium cell 6 years operative and operate battery backup 1 channel day clock with 14 memory programme, suitable to operate on 240V + 5%, 16A with, floating contacts Minimum switching setup time 1 minimum & LCD display. Also comprised permanent ON/OFF switching. Programming switches & housed in fire proof thermoplastic enclosure & transparent cover erected as required with necessary connection erected as directed. | No.
H | 25 Amp DP Dinrail Mounted Contactor | No.
J | SITC of 40 Amp DP Dinrail Mounted Contactor | No.
K | SITC of IP65 Polycarbonate enclosure for DP MCB | No.
L | SITC of IP65 Polycarbonate enclosure for FP MCB | No.
M | SITC of IP65 Polycarbonate enclosure for FP MCCB | No.
N | SITC Of 32A x 250 Volt single phase Power socket outlet point having IP rating of IP:65 at convenient location with MCB.for outdoor duty. | No.
P | SITC Of 32A x 415 Volt three phase Power socket outlet point having IP rating of IP:65 at convenient location with MCB.for outdoor duty. | No.
Q | SITC of 63 Amp FP Isolator with IP65 Enclosure | No.
R | SITC of 40 Amp FP Isolator with IP65 Enclosure | No.
S | Cable Trench Making trench in soft soil of suitable width of 90 cms deep for laying cable or locating the fault all over the run and backfilling the same and making the surface proper. Providing and erecting iron clad cable route marker duly marked with ELE.CABLE of size 23 cms.X 12 cms. Flushed with ground in cement foundation as directed by Engineer in charge. The width shall be as per requirement | m
C/F
B/F
A | Covering of cable with second class bricks laid cover the cable crosswise & also on both sides with covering of 7. 5 Cms. layer of sand above & below cable (cable shall be laid in 0.9mtr.deep & 0.4 Mtr.wide trench). Where there are more than one cable in the trench on either side of the cable, 5 Cms. over lapping of bricks shall be provided. | m
B | Construction of brick masonry pulling chamber 450 mm x 450 mm inside clear size and depth up to 0.6 meter with 350 mm thick masonry in cement mortar proportion 1:5,cement finish cement plaster in CM proportion of 15 mm thickness from inside with 150 mm thick PCC at bottom with top slab minimum 200 mm thickness in M20 grade with reinforcement. The rate shall be inclusive of providing and fixing frame and 450 mm dia cover of FRC for the Heavy Duty. Rate also inclusive of excavation and back filling & clearing the site by removing debris & Shifting of the debris & making site good As per the Instruction of the Engineer In charge complete in all respect. | No.
C | Construction of brick masonry pulling chamber 600 mm x 600 mm inside clear size and depth up to 0.60 meter with 350 mm thick masonry in cement mortar proportion 1:5,cement finish cement plaster in CM proportion of 15 mm thickness from inside with 150 mm thick PCC at bottom with top slab minimum 200 mm thickness in M20 grade with reinforcement. The rate shall be inclusive of providing and fixing frame and 600 mm dia cover of FRC for the Heavy Duty. Rate also inclusive of excavation and back filling & clearing the site by removing debris & Shifting of the debris & making site good As per the Instruction of the Engineer In charge complete in all respect. | No.
D | Construction of brick masonry pulling chamber 750 mm x 750 mm inside clear size and depth up to 0.75 meter with 350 mm thick masonry in cement mortar proportion 1:5,cement finish cement plaster in CM proportion of 15 mm thickness from inside with 150 mm thick PCC at bottom with top slab minimum 200 mm thickness in M20 grade with reinforcement. The rate shall be inclusive of providing and fixing frame and 750 mm dia cover of FRC for the Heavy Duty. Rate also inclusive of excavation and back filling & clearing the site by removing debris & Shifting of the debris & making site good As per the Instruction of the Engineer In charge complete in all respect. | No.
E | Construction of brick masonry pulling chamber 1000 mm x 1000 mm inside clear size and depth up to 1.0 meter with 350 mm thick masonry in cement mortar proportion 1:5,cement finish cement plaster in CM proportion of 15 mm thickness from inside with 150 mm thick PCC at bottom with top slab minimum 200 mm thickness in M20 grade with reinforcement. The rate shall be inclusive of providing and fixing frame and 900 mm dia cover of FRC for the Heavy Duty. Rate also inclusive of excavation and back filling & clearing the site by removing debris & Shifting of the debris & making site good As per the Instruction of the Engineer In charge complete in all respect. | No.
F | Cable Tray Providing and fixing approved make Ladder type cable tray. Made from M.S sheet. The cable tray should be bended as per IS 2062/1079 shall be fabricated of double bended channel section longitudinal members with single bended Channel section. Rungs of members welded to the base of tha longitudinal members at 250 mm c/c spacing . as per IS and shall be coated with hot dip galvanizing as per IS 2629/4759. with coupler plate / Fish plate and GI hardware like nut - bolt and washers etc. erected on existing support as per Specification and as per instruction of engineer in charge.. 750 X 100 X 2 mm Thick | m
G | 600 X 100 X 2 mm Thick | m
H | 400 X 100 X 2 mm Thick | m
J | Providing and fixing approved make Perforated C type cable tray. Made from CR sheet steel. The cable tray should be single or double bended as per required and as per IS 2062/1079 and shall be coated with hot dip galvanizing as per IS 2629/4759. with coupler plate / Fish plate and GI hardware like nut - bolt and washers etc. erected on existing support as per Specification and as per instruction of engineer in charge.. (2) 100 X 50 X 1.6 mm Thick | m
K | (5) 300 X 50 X 2 mm Thick | m
L | (6) 450 X 50 X 2 mm Thick | m
C/F
B/F
A | (7) 600 X 50 X 2 mm Thick | m
B | Fabrication Supplying , fabricating and installation of various sizes MS race way / junction boxes/clamps/hangers for Cable Tray, Light Fixture made out of specified size sheet/Angle/Flat/rod/ channel etc as per design with all necessary accessories like bend, junction boxes, coupler, Anchor fastener, Bolt Nuts, etc.. & work from MS structure for other work with anchor fastener of Hilti make and necessary hardware with necessary welding has to be done to complete the job from ISA / ISMC / PLATE. The job also includes to paint the structure with two coats of red oxide and two coats color of enamel paint as approved and recommended by consultant. Complete in all respect to be installed at any height with all necessary arrangements. Contractor has to complete the work up to satisfaction of Consultant | kg
C | Cables Providing and erecting XLPE(IS:7098)(I)-88 ISI armoured cable multistrand Aluminium conductor for 1.1 KV. to be laid on wall with necessary clamps or in existing trench / pipe of following size of cables 240 sq.mm x 3.5c Al. XLPE Arm. Cable | m
D | 185 sq.mm x 3.5c Al. XLPE Arm. Cable | m
E | 150 sq.mm x 3.5c Al. XLPE Arm. Cable | m
F | 120 sq.mm x 3.5c Al. XLPE Arm. Cable | m
G | 70 sq.mm x 3.5c Al. XLPE Arm. Cable | m
H | 50 sq.mm x 3.5c Al. XLPE Arm. Cable | m
J | 35 sq.mm x 3.5c Al. XLPE Arm. Cable | m
K | 25 sq.mm x 4 c Al. XLPE Arm. Cable | m
L | 16 sq.mm x 4 c Al. XLPE Arm. Cable | m
M | 10 sq.mm x 4 c Al. XLPE Arm. Cable | m
N | Providing & erecting XLPE(IS:7098) (I)-88 ISI armoured cable multistrand copper conductor for 1.1 KV. To be laid on wall with necessary clamps or in existing trench / pipe at road crossing or floor of following size cable. 16 sq.mm x 4 c cu. XLPE Arm. Cable | m
P | 10 sq.mm x 4 c cu. XLPE Arm. Cable | m
Q | 6 sq.mm x 4 c cu. XLPE Arm. Cable | m
R | 4 sq.mm x 4 c cu. XLPE Arm. Cable | m
S | 6 sq.mm x 3 c cu. XLPE Arm. Cable | m
T | 4 sq.mm x 3 c cu. XLPE Arm. Cable | m
U | 50 Sq.mm. x 4 c XLPE Cu. Flexible Cable | m
V | 16 Sq.mm. x 4 c XLPE Cu. Flexible Cable | m
W | providing and erecting Mains with ISI marked, 1.5KV grade electrolyte multi stranded, annealed copper conductor with heat resistant PVC insulated conforms to IS 694, IEC - 227 erected in existing pipe of following size (Specifically for control panel, relays, power switchgears, motor starters & control wiring) with required size of copper lugs, nuts and bolts if required. (a) One wire 1.00 sq. mm | m
X | (b) One wire 1.50 sq. mm | m
C/F
B/F
A | Supplying & erecting XLPE (IS:7098)(I)-88 ISI unarmoured copper cable 1.1 KV grade to be erected as directed of following size 3 core 2.5 Sq.mm. | m
B | Cable Termination SITC of Cable end termination of the following XLPE insulated PVC sheathed aluminum/copper conductor armored cables of 1100 volt grade including supplying and fixing of bimetallic Long neck crimping lugs, double compression type Brass glands with earthing. 240 sq.mm x 3.5c Al. XLPE Arm. Cable | No.
C | 185 sq.mm x 3.5c Al. XLPE Arm. Cable | No.
D | 150 sq.mm x 3.5c Al. XLPE Arm. Cable | No.
E | 120 sq.mm x 3.5c Al. XLPE Arm. Cable | No.
F | 70 sq.mm x 3.5c Al. XLPE Arm. Cable | No.
G | 50 sq.mm x 3.5c Al. XLPE Arm. Cable | No.
H | 50 sq.mm x 4c Cu. Flexible Cable | No.
J | 35 sq.mm x 3.5c Al. XLPE Arm. Cable | No.
K | 25 sq.mm x 4 c Al. XLPE Arm. Cable | No.
L | 16 sq.mm x 4 c Al./ Cu. XLPE Arm. Cable | No.
M | 10 sq.mm x 4 c Al./ Cu. XLPE Arm. Cable | No.
N | 6 sq.mm x 4 c Cu. XLPE Arm. Cable | No.
P | 4 sq.mm x 4 c Cu. XLPE Arm. Cable | No.
Q | 6 sq.mm x 3 c Cu. XLPE Arm. Cable | No.
R | 4 sq.mm x 3 c Cu. XLPE Arm. Cable | No.
S | SITC of Cable end termination of the following XLPE insulated PVC sheathed aluminum/copper conductor armored cables of 1100 volt grade including supplying and fixing of bimetallic Long neck crimping lugs, double compression type Brass glands with earthing. 3 core 2.5 Sq.mm. | No.
c/f
b/f
MV Switchgear & Power Panels (TTA as per IEC 61439)
Supply, Unloading at site, shifting to site, assembling, leveling, grouting, erecting, Testing, & Commissioning main L.T. panel board, fabricated from M.S. sheet & folded channel totally enclosed cubical type compartmentalized. Scope Covers Unloading at Site, Store in Weather Proof Condition, Shift to the Location Basement / GF / FF, Grouting, Installation, Testing & Commissioning complete in all respect & As per the instruction of Architect / Consultant / Engineer Incharge. Scope also covers Co ordination with Panel Manufacturer.
Design, fabrication, assembling, supply, installation , testing of Panels for 415 V, 3 phase, 50 Hz, 4 wire power supply system.
Panels shall be fabricated out of 2 mm thick CRCA sheet steel in cubical formation, compartmentalized in Form 4b Construction, floor mounted, free standing and shall be dust and vermin proof. 3 mm thick cable gland plate, shall be provided both at the top and the bottom of the panel.
All large panels shall be provided with lifting hooks. Distribution panels shall be fabricated in accordance with the specifications.
Note : Panel vendor has to provide Surge Protection at every stage of the Distribution.
1) Supporting rigid steel framework.
2) Cubicle type, 14 gauge CRCA sheet steel enclosed.
3) Complete with interconnections and distribution bus bars.
4) Proper bonding to earth.
5) Painting/lettering on Breakers and distribution boards, the location they serve, providing on each panel its circuit diagram.
6) Providing cable clamps / supports within distribution boards cable alley.
7) TPN ACB’s / MCCB’s shall mean 3 pole ACB’s / MCCB’s with adequate size of neutral link.
8) All MCB’s shall be of minimum 10 KA breaking capacity.
9) The breaking capacity of MCCB’s are mentioned panel wise.
10) All motor feeders MCCBs shall be of motor duty.
11) Distribution panels shall be Powder Coated with Siemens gray paint shade no. RAL-7032 of IS-5.
12) Degree of protection for following type of distribution panel enclosure shall be as per IS:13947-1993. a) IP 52 for indoor panels. b) IP 54 for Service area panels. c) IP 65 for outdoor panels.
13) All MCCB’s shall be provided with operating mechanism for door interlock & with the roraty handle.
14) Current density of aluminium shall be 1 sq mm for 0.8 amps for rated current of bus bars and current density of copper shall be 1 sq.mm for 1 amps for rated current of bus bars.
15) Tinned copper earth bus as specified in the BOQ / SLD shall be provided through out the length of each board.
16) All measuring instruments (Meters) shall be of digital electronic with LED of approved make and compatible with BAS.
17) All hinged door shall be earthed through 2.5 sq mm tinned braided copper wire.
18) All panels shall have provision of the following: a) IP 55 for outdoor panels. b) Pad locking of MCCB’s handles in “OFF” Position.
19) Additional set of C.T.s, potential free contacts, connectors, contactors with wiring etc are to be provided for BAS including space required for various transducers in Main Switch Board sections. Only transducers shall be supplied by BAS contractor.
20) All the C.T.s should be auto short link type.
21) All the MCCB's should be with rotary handle.
22) All MCB’s used for protection of resistive and lightly inductive load shall be type “B” characteristic and inductive (motor) load shall be of type “C” characteristic and discharge lamps and UPS etc. shall be of type D characteristic.
C/F
B/F
23) All incoming and outgoing air circuit breakers shall be placed on middle portion of the vertical in single tier formation.
24) All PTs / control transformer shall be provided with centre tap earth secondary.
25) If Any descripancy found in SLD & BOQ, it should be brought in the notice of the Client / Consultant, Client / Consultant's decision will be final in case of any descripancy. 26) All outdoor panles should be provided with minimum 600mm height fabrication stand with all side 2mm thick M.S. powder coated sheet.
26) G.A. Drawing should be checked & Finalised by consultant before fabrication.
A | SITC of Main LT Panel Incoming : From CSS 1250 amps FP ACB (50 KA) with following accessories: 1 Sets i. LED type Phase indicating & ON, OFF light shall be protected by 2 amps SP MCB's. - 5 nos. ii. 3 Nos. of Digital type 0-1250 / 5 amps CTR digital ammeter with 3 nos 1250 / 5 amps, 15 VA Class I CT’s. iii. Digital type 0-500 Volt digital voltmeter with inbuilt selector switch & shall be protected by 2 amp TP MCB’s - 1 no. iv) Load Manager of Schneider make PM 5110 with RS 485 connectivity with 3 nos. of Class 1, 1250 / 5 Amp. CT of 15 VA Bus Bars 1250 amps FP Al. bus bars with colored heat shrinkable insulated sleeve. | No.
Incoming : From D.G. 1250 amps FP ACB (50 KA) with following accessories: 1 Sets i. LED type Phase indicating & ON, OFF light shall be protected by 2 amps SP MCB's. - 5 nos. ii. 3 Nos. of Digital type 0-1250 / 5 amps CTR digital ammeter with 3 nos 1250 / 5 amps, 15 VA Class I CT’s. iii. Digital type 0-500 Volt digital voltmeter with inbuilt selector switch & shall be protected by 2 amp TP MCB’s - 1 no. iv) Load Manager of Schneider make PM 5110 with RS 485 connectivity with 3 nos. of Class 1, 1250 / 5 Amp. CT of 15 VA
Outgoing : 630 amps 4 pole MCCB ( 50 KA) : 3 Nos. 400 amps 4 pole MCCB ( 36 KA) : 2 Nos. 320 amps 4 pole MCCB ( 36 KA) : 1 Nos. 200 amps 4 pole MCCB ( 25 KA) : 2 Nos. 63 amps 4 pole MCCB (16KA) : 5 Nos. 40 amps 4 pole MCCB (16KA) : 5 Nos. 32 amps 4 pole MCB ( 10 KA ) : 5 Nos. 6 to 32 amps 2 pole MCB ( 10 KA) : 6 Nos. Panel should be as per SLD & Specifications
B | SITC of Equipment Power Panel Incoming : 400 amps FP MCCB (36 KA) with following accessories: 1 Sets i. LED type Phase indicating & ON, OFF light shall be protected by 2 amps SP MCB's. - 5 nos. ii. 3 Nos. of Digital type 0-500 / 5 amps CTR digital ammeter with 3 nos 400 / 5 amps, 15 VA Class I CT’s. iii. Digital type 0-500 Volt digital voltmeter with inbuilt selector switch & shall be protected by 2 amp TP MCB’s - 1 no. iv) Load Manager of Schneider make PM 5110 with RS 485 connectivity with 3 nos. of Class 1, 400 / 5 Amp. CT of 15 VA Bus Bars 400 amps FP Al. bus bars with colored heat shrinkable insulated sleeve. TVSS (100KA) Ten Mode 330 Series of ASCO Make Unit with 100A FP MCCB as per SLD Outgoing 125 amp 4 pole MCCB ( 16 KA : 4 Nos. 32 amps 4 pole MCB ( 10 KA ) : 12 Nos. 25 amps 4 pole MCB ( 10 KA ) : 3 Nos. 40 amps 2 pole MCB ( 10 KA ): 2 Nos. 6 to 32 amps 2 pole MCB ( 10 KA ): 2 Nos. Panel should be as per SLD & Specifications | No.
c/f
b/f
A | SITC of Lighting Power Panel Incoming : 200 amps FP MCCB (25 KA) with following accessories: 1 Sets i. LED type Phase indicating & ON, OFF light shall be protected by 2 amps SP MCB's. - 5 nos. ii. 3 Nos. of Digital type 0-500 / 5 amps CTR digital ammeter with 3 nos 200 / 5 amps, 15 VA Class I CT’s. iii. Digital type 0-500 Volt digital voltmeter with inbuilt selector switch & shall be protected by 2 amp TP MCB’s - 1 no. iv) Load Manager of Schneider make PM 5110 with RS 485 connectivity with 3 nos. of Class 1, 200 / 5 Amp. CT of 15 VA Bus Bars 200 amps FP Tinned copper bus bars with colored heat shrinkable insulated sleeve. TVSS (100KA) Ten Mode 330 Series of ASCO Make Unit with 100A FP MCCB as per SLD Outgoing 63 amps 4 pole MCB ( 10 KA ) : 3 Nos. 40 amps 4 pole MCB ( 10 KA ) : 9 Nos. 32 amps 4 pole MCB ( 10 KA ) : 2 Nos. 40 amps 2 pole MCB ( 10 KA ): 2 Nos. 6 to 32 amps 2 pole MCB ( 10 KA ): 2 Nos. Panel should be as per SLD & Specifications | No.
B | SITC of 350KVAR APFCR Panel Design, Supplying, installing, testing of factory fabricated ready made Three phase APFC Panel Cubical Panel fabrication should be type tested as per IEC 61921, 61439:1&2 Capacitor Duty Contactor for switching as per following Steps Incomer Switch of MCCB type Icu=Ics=50KA at 400/440 Volts, with OC, SC, internal earth fault protection Incomer Switch of MCCB type Icu=Ics=50KA at 400/440 Volts, with OC, SC, internal earth fault protection,Copper tinned insulated Busbar,Cubical panel should be indoor type with IP 43 and IK 10,Metalized polypropylene film tye3-phase 550Volt Capacitor,De tuning Reactor for each capacitor,Panel having Short Circuit and Overload protection,Each step Capacitor having suitable MCB with Sc, OL, internal earth fault relay,Each stage having Stage Contactor (Capacitor load rating),PF regulator master controller having suitable steps with LCD display, Rs 485 Communication port, Indication LED Lamps for main incomer and ON-OFF for each capacitor bank,MS Chanel for Floor mounting, Cable entry as per site situation,Cooling fans for panel 350KVAR . | No.
C/F
B/F
A | SITC of Lighting Panel (TTA as per IEC 61439) Incoming : 250 amps FP MCCB (25 KA) with following accessories: 1 Sets i. LED type Phase indicating & ON, OFF light shall be protected by 2 amps SP MCB's. - 5 nos. ii. 3 Nos. of Digital type 0-500 / 5 amps CTR digital ammeter with 3 nos 250 / 5 amps, 15 VA Class I CT’s. iii. Digital type 0-500 Volt digital voltmeter with inbuilt selector switch & shall be protected by 2 amp TP MCB’s - 1 no. iv) Load Manager of Schneider make PM 5110 with RS 485 connectivity with 3 nos. of Class 1, 250 / 5 Amp. CT of 15 VA Bus Bars 250 amps FP Tinned copper bus bars with colored heat shrinkable insulated sleeve. TVSS (100KA) Ten Mode 330 Series of ASCO Make Unit with 100A FP MCCB as per SLD Outgoing 63 amps 4 pole MCB ( 10 KA ) : 3 Nos. 40 amps 4 pole MCB ( 10 KA ) : 7 Nos. 32 amps 4 pole MCB ( 10 KA ) : 32 Nos. 40 amps 2 pole MCB ( 10 KA ): 2 Nos. 6 to 32 amps 2 pole MCB ( 10 KA ): 45 Nos. Panel should be as per SLD & Specifications | No.
B | SITC of IP65 HVAC Panel Incoming : 630 amps FP MCCB (25 KA) with following accessories: 1 Sets i. LED type Phase indicating & ON, OFF light shall be protected by 2 amps SP MCB's. - 5 nos. ii. 3 Nos. of Digital type 0-500 / 5 amps CTR digital ammeter with 3 nos 630 / 5 amps, 15 VA Class I CT’s. iii. Digital type 0-500 Volt digital voltmeter with inbuilt selector switch & shall be protected by 2 amp TP MCB’s - 1 no. iv) Load Manager of Schneider make PM 5110 with RS 485 connectivity with 3 nos. of Class 1, 250 / 5 Amp. CT of 15 VA Bus Bars 630 amps FP Tinned copper bus bars with colored heat shrinkable insulated sleeve. TVSS (100KA) Ten Mode 330 Series of ASCO Make Unit with 63A FP MCB as per SLD Outgoing 63 amps 4 pole MCB ( 10 KA ) : 20 Nos. 40 amps 4 pole MCB ( 10 KA ) : 4 Nos. Panel should be as per SLD & Specifications | No.
C | SITC of IP 65 External Area lighting Panel Incoming : 63 amps FP MCB (16 KA) with following accessories: 1 Sets LED type Phase indicating & ON, OFF light shall be protected by 2 amps SP MCB's. 3 Nos. of Digital type 0-63 / 5 amps CTR digital ammeter with 3 nos 63 / 5 amps, 15 VA Class I CT’s. Digital type 0-500 Volt digital voltmeter with inbuilt selector switch & shall be protected by 2 amp TP MCB’s Bus Bars 63 amps FP Tinned copper bus bars with coloured heat shrinkable insulated sleeve. TVSS (100KA) Ten Mode 330 Series of ASCO Make Unit with 63A FP MCB as per SLD Outgoing 40 to 63 amps 4 pole MCB ( 10 KA ) : 6 No. 6 to 32 amps FP 4 pole MCB : 2 no. 40 to FP Contactor : 6 no. Dual channel Timer : 3 nos. Panel should be as per SLD | No.
C/F
B/F
A | SITC of Plumbing Panel Incoming : 200 amps FP MCCB (25 KA) with following accessories: 1 Sets i. LED type Phase indicating & ON, OFF light shall be protected by 2 amps SP MCB's. - 5 nos. ii. 3 Nos. of Digital type 0-500 / 5 amps CTR digital ammeter with 3 nos 200 / 5 amps, 15 VA Class I CT’s. iii. Digital type 0-500 Volt digital voltmeter with inbuilt selector switch & shall be protected by 2 amp TP MCB’s - 1 no. iv) Load Manager of Schneider make PM 5110 with RS 485 connectivity with 3 nos. of Class 1, 200 / 5 Amp. CT of 15 VA Bus Bars 200 amps FP Tinned copper bus bars with colored heat shrinkable insulated sleeve. TVSS (100KA) Ten Mode 330 Series of ASCO Make Unit with 63A FP MCB as per SLD Outgoing 63 amps 4 pole MCB ( 10 KA ) : 3 No. 40 amps 4 pole MCB ( 10 KA ) : 3 No. 6 to 32 amps 4 pole MCB ( 10 KA ): 4 Nos. 6 to 32 amps 2 pole MCB ( 10 KA ): 2 Nos. Panel should be as per SLD & Specifications | No.
B | SITC of Fire Pump Panel Incoming : 320 amps FP MCCB (36 KA) with following accessories: 1 Sets i. LED type Phase indicating & ON, OFF light shall be protected by 2 amps SP MCB's. - 5 nos. ii. 3 Nos. of Digital type 0-500 / 5 amps CTR digital ammeter with 3 nos 320 / 5 amps, 15 VA Class I CT’s. iii. Digital type 0-500 Volt digital voltmeter with inbuilt selector switch & shall be protected by 2 amp TP MCB’s - 1 no. iv) Load Manager of Schneider make PM 5110 with RS 485 connectivity with 3 nos. of Class 1, 320 / 5 Amp. CT of 15 VA Bus Bars 320 amps FP Al. bus bars with colored heat shrinkable insulated sleeve. TVSS (100KA) Ten Mode 330 Series of ASCO Make Unit with 63A FP MCB as per SLD Outgoing 250 amp 4 Pole MCCB (25 KA) : 1 no. 63 amps 4 pole MCB ( 10 KA ) : 2 No. 6 to 32 amps 2 pole MCB ( 10 KA ): 2 Nos. Panel should be as per SLD & Specifications | No.
C | Light Fixture Supplying and erecting LED indoor fittings with LEDs of wattage 0.2 Watt to 0.5 Watt assembled on single MCPCB, with housing used as a heat sink shall be made of thick sheet Steel conforming to IS: 513/CRCA/ aluminium die cast powder coated and high U.V. & corrosion resistance with diffuser with company mark/name 160V to 270V, Power Factor more than 0.95, THD < 15%, CCT 3000 K to 6500K, Luminaire efficacy> 85 lumens/watt ,LED LED driver efficiency > 85 % ( fitting required LM-79 & LM-80 Certificates)(NOTE: Below description have shown ranges of Wattage capacity of LED fittings.The Engineer incharge may select any wattage capacity between the ranges shown.) (A) Tube Light with integral driver (i) 5-10 Watts, Surge-2 KV, IP-20, conventional 1 to 2 feet. Cat-lll | No.
D | Supplying and erecting LED indoor fittings with LEDs of wattage 0.2 Watt to 0.5 Watt assembled on single MCPCB, with housing used as a heat sink shall be made of thick sheet Steel conforming to IS: 513/CRCA/ aluminium die cast powder coated and high U.V. & corrosion resistance with diffuser with company mark/name 160V to 270V, Power Factor more than 0.95, THD < 15%, CCT 3000 K to 6500K, Luminaire efficacy> 85 lumens/watt ,LED LED driver efficiency > 85 % ( fitting required LM-79 & LM-80 Certificates)(NOTE: Below description have shown ranges of Wattage capacity of LED fittings.The Engineer incharge may select any wattage capacity between the ranges shown.) (A) Tube Light with integral driver (iv) 22-24 Watts, Surge - 2KV,IP-20, conventional 4 feet. Cat-lll | No.
c/f
b/f
A | Supplying and erecting LED indoor fittings with LEDs of wattage 0.2 Watt to 0.5 Watt assembled on single MCPCB, with housing used as a heat sink shall be made of thick sheet Steel conforming to IS: 513/CRCA/ aluminium die cast powder coated and high U.V. & corrosion resistance with diffuser with company mark/name 160V to 270V, Power Factor more than 0.95, THD < 15%, CCT 3000 K to 6500K, Luminaire efficacy> 85 lumens/watt ,LED LED driver efficiency > 85 % ( fitting required LM-79 & LM-80 Certificates)(NOTE: Below description have shown ranges of Wattage capacity of LED fittings.The Engineer incharge may select any wattage capacity between the ranges shown.) (A) Tube Light with integral driver (v) 36-40 Watts, Surge-2 KV, IP-20, conventional 4 feet. Cat-lll | No.
B | Supplying and erecting LED indoor fittings with LEDs of wattage 0.2 Watt to 0.5 Watt assembled on single MCPCB, with housing used as a heat sink shall be made of thick sheet Steel conforming to IS: 513/CRCA/aluminium pressure die cast powder coated and high U.V. & corrosion resistance with diffuser housed in aluminium casted body with company mark/name 160V to 270V,Power Factor more than 0.95, THD < 15 %, CCT 3000 K to 6500K, Luminaire efficacy> 85 lumens/watt , LED driver efficiency > 85 % ( fitting required LM-79 & LM-80 Certificates)(NOTE: Below description have shown ranges of Wattage capacity of LED fittings.The Engineer incharge may select any wattage capacity between the ranges shown.) (A) Square/ Circular shaped Surface/Recessed Mount Downlight with provision for spring loaded mounting clips complete.IP20 (i) 5-9 watts,Surge-2 KV. Cat-lll | No.
C | Supplying and erecting LED indoor fittings with LEDs of wattage 0.2 Watt to 0.5 Watt assembled on single MCPCB, with housing used as a heat sink shall be made of thick sheet Steel conforming to IS: 513/CRCA/aluminium pressure die cast powder coated and high U.V. & corrosion resistance with diffuser housed in aluminium casted body with company mark/name 160V to 270V,Power Factor more than 0.95, THD < 15 %, CCT 3000 K to 6500K, Luminaire efficacy> 85 lumens/watt , LED driver efficiency > 85 % ( fitting required LM-79 & LM-80 Certificates)(NOTE: Below description have shown ranges of Wattage capacity of LED fittings.The Engineer incharge may select any wattage capacity between the ranges shown.) (A) Square/ Circular shaped Surface/Recessed Mount Downlight with provision for spring loaded mounting clips complete.IP20 (ii) 11-15 watts, Surge-2 KV .Cat-lll | No.
D | Supplying and erecting LED indoor fittings with LEDs of wattage 0.2 Watt to 0.5 Watt assembled on single MCPCB, with housing used as a heat sink shall be made of thick sheet Steel conforming to IS: 513/CRCA/aluminium pressure die cast powder coated and high U.V. & corrosion resistance with diffuser housed in aluminium casted body with company mark/name 160V to 270V,Power Factor more than 0.95, THD < 15 %, CCT 3000 K to 6500K, Luminaire efficacy> 85 lumens/watt , LED driver efficiency > 85 % ( fitting required LM-79 & LM-80 Certificates)(NOTE: Below description have shown ranges of Wattage capacity of LED fittings.The Engineer incharge may select any wattage capacity between the ranges shown.) (A) Square/ Circular shaped Surface/Recessed Mount Downlight with provision for spring loaded mounting clips complete.IP20 (iii) 16-20 watts, Surge-2 KV . Cat-lll | No.
C/F
B/F
A | Supplying and erecting LED indoor fittings with LEDs of wattage 0.2 Watt to 0.5 Watt assembled on single MCPCB, with housing used as a heat sink shall be made of thick sheet Steel conforming to IS: 513/CRCA/aluminium pressure die cast powder coated and high U.V. & corrosion resistance with diffuser housed in aluminium casted body with company mark/name 160V to 270V,Power Factor more than 0.95, THD < 15 %, CCT 3000 K to 6500K, Luminaire efficacy> 85 lumens/watt , LED driver efficiency > 85 % ( fitting required LM-79 & LM-80 Certificates)(NOTE: Below description have shown ranges of Wattage capacity of LED fittings.The Engineer incharge may select any wattage capacity between the ranges shown.) (A) Square/ Circular shaped Surface/Recessed Mount Downlight with provision for spring loaded mounting clips complete.IP20 (iv) 22-24 watts, Surge-2 KV. Cat-lll | No.
B | Providing and erecting PVC body surface or pendent mounting LED Bulk type 9 watt Lighting Fitting with electronic driver. And lumen output from luminaire 720lm , input voltage range 90-300VAC , 50Hz cool white(3000 to 6500k), inbuilt driver, -20degC to +60degC working temperature, AL frame with Beam Angle 120deg | No.
C | Supplying, installing, testing and commissioning of 35 W surface-mounted LED downlight, IP65 protection rating, suitable for indoor/outdoor use, with system efficacy ≥100 lm/W, high-purity reflector and integral control gear. The luminaire shall have minimum 50,000 hours life (L70B50 @ 25°C), CRI ≥ 80, colour temperature 3000/4000/6500 K (as specified), and corrosion-resistant powder-coated housing. The fitting shall operate on 230 V AC, 50 Hz, include all necessary accessories, mounting hardware and make complete in all respects as per specification and engineer’s direction. | No.
D | Supplying and erecting LED street light / Flood light fittings with High power White LEDs wattage of 3 Watt and above assembled on single MCPCB, efficiency more than 130 lm/w and corrosion free High pressure die cast aluminum housing with smooth finish powder coated and heat sink extruded aluminium with diffuser and Polycarbonate optics/ lenses, with toughened glass with company mark/name engraved or embossed 160 to 270 V,Power Factor more than 0.95, THD < 10 %, CCT 3000 K to 5700K,Uniformity ratio >0.45, Luminaire efficacy> 100 lumens/watt . LED driver efficiency > 85 %.( fittings required LM-79 & LM-80 certificates)(NOTE: Below description have shown ranges of Wattage capacity of LED fittings.The Engineer incharge may select any wattage capacity between the ranges shown.) (A) Street Light (IP-65), Surge protection -4KV integral and ,Light must have 440VAC line supply with over-voltage protection. (iii) Above 60 to 90 watts Cat-lll | No.
E | Supplying and erecting LED street light / Flood light fittings with High power White LEDs wattage of 3 Watt and above assembled on single MCPCB, efficiency more than 130 lm/w and corrosion free High pressure die cast aluminum housing with smooth finish powder coated and heat sink extruded aluminium with diffuser and Polycarbonate optics/ lenses, with toughened glass with company mark/name engraved or embossed 160 to 270 V,Power Factor more than 0.95, THD < 10 %, CCT 3000 K to 5700K,Uniformity ratio >0.45, Luminaire efficacy> 100 lumens/watt . LED driver efficiency > 85 %.( fittings required LM-79 & LM-80 certificates)(NOTE: Below description have shown ranges of Wattage capacity of LED fittings.The Engineer incharge may select any wattage capacity between the ranges shown.) (B) Flood Light (IP-65), Surge protection -4KV integral and ,Light must have 440VAC line supply with over-voltage protection. (iii) Above 60 to 90 watts Cat-lll | No.
c/f
b/f
A | Supplying and erecting LED street light / Flood light fittings with High power White LEDs wattage of 3 Watt and above assembled on single MCPCB, efficiency more than 130 lm/w and corrosion free High pressure die cast aluminum housing with smooth finish powder coated and heat sink extruded aluminium with diffuser and Polycarbonate optics/ lenses, with toughened glass with company mark/name engraved or embossed 160 to 270 V,Power Factor more than 0.95, THD < 10 %, CCT 3000 K to 5700K,Uniformity ratio >0.45, Luminaire efficacy> 100 lumens/watt . LED driver efficiency > 85 %.( fittings required LM-79 & LM-80 certificates)(NOTE: Below description have shown ranges of Wattage capacity of LED fittings.The Engineer incharge may select any wattage capacity between the ranges shown.) (B) Flood Light (IP-65), Surge protection -4KV integral and ,Light must have 440VAC line supply with over-voltage protection. (iv) above 90 to 120 watts Cat-lll | No.
B | Exhaust Fans : Supplying & erecting approved make low noise decorative exhaust fan having size 200mm with 1350 RPM with square frame ABS body with inbuilt lowers & square frame. | No.
C | Supplying & erecting single phase approved make industrial exhaust fan suitable for medium duty ring mounted low noise operation suitable for medium duty having following dia size and maximum speed in RPM [A] 305 mm dia 900 RPM | No.
D | [D] 450 mm dia 900 RPM with louvers | No.
E | Supply, Installation, Testing and Commissioning of suitable sweep, BEE 5 Star rated, Ceiling fan with Brush Less Direct Current (BLDC) permanent ferrite magnet Motor, class of insulation: B, Rust free 3 nos.Aluminium blades, 2 nos. canopies, shackle kit with earthing provision, copper winding, Power factor not < 0.9, Service Value (CMM/W) minimum 6.85, Air delivery minimum 215 CMM, 350 RPM,230v (tolerance as per IS : 374-2019), THD < 10%, with remote unit for Speed Control and all remaining accessories including safety pin, nut bolts, washers, temperature rise = 75 degree C (Max.), suitable for 140 to 285 Voltage and rectifier circuit with surge, over current and overload protection , 50 Hz, Single phase AC Supply, earthing etc. Complete as required.[ Make shall be approved by Engineer in Charge] (B) 1200 mm Sweep (48") | No.
F | Supplying and erecting 19 / 20 mm. nominal bore Medium Class M.S. Pipe down rod erected duly painted for fan complete with necessary 24/ O.20, 3 core flexible wire with earthing. | m
G | Street Light Pole Supplying and erecting approved make Conical Pole (Medium Duty ) Made from HR sheet steel. The pole should be made as per IS. and shall be coated with hot dip galvanizing as per IS 2629/2633/4759, with required base plate and integral Junction box consist of terminal plate of min 6mm Hylam sheet, standard profile 35mmX7.5mm Din-Rail for MCB Mounting, stud type terminal and arrangement for cable terminations as erected on suitable foundation (included) with necessary GI nut-bolts/J-Bolts. as per details given by manufacturer considering site requirement. The length of poles are as below. (D) 6 Mtr. Long 70 mm Top X 160 mm bottom dia, 3 mm thickness | No.
H | Providing and erecting Street Light pole bracket comprising main B Class GI pipe of 4.2 cm/require outside dia. complete with suitable B Class G.I. sleeve tubing of approx. 45cms.length and suitable for 76.5 mm /80mm / required size of pole top having sufficient fasteners for fixing the brackets and having spread of 1.5.mtr. length with 110 deg.with vertical plane & suitable welded stays, reducer and with check nuts complete painted with one coat of Red oxide / PU base primer and two coats of Aluminium / PU paint. paint with following nos of arms. [A] Single Arm Bracket 1.5 Mtr | No.
J | Providing cement concrete.for foundation or for concrete filling in 1:2:4 ratio with 20 to 25 mm stone metal duly plastered with necessary curing for pole muffing or any other purpose. | m3
c/f
b/f
A | TMT Bar for Pole Foundation | Kg.
B | CSS Supply of 1000 KVA Outdoor type Compact Substation consisting of Transformer,HT switchgear and LT Switchgear and confirming to IEC-62227. a) Transformer: 1000 KVA Copper wound 11KV /433 V DYn11, Dry Cast resin type Transformer with tapping range +10 to -10% @ 2.5% ( with tolerance), with OLTC with RTCC Panel, class F , with surge restorers, Digital WTI, IS1171 as per b) HT Compartment: 11KV, 21kA for 3 Sec . 630 A 50 Hz, gas insulated VCB in SS tank in sheet enclosure having provision for one no. direct connection of Incoming supply cable upto 300sq mm and one no. VCB( Manually charging & closing) in series with LBS between VCB and Transformer, Self Powered Relay 3 O/C +1 E/F Relay type CSPR-V5, mechanical ON/OFF indicator, trip coil , Manual Close & Trip PB, live cable indicator, mechanical interlocks, pad locking facility, SF6 gas manometer, cable boots, 3 nos. CTs with Ratio -/1A, Cl: 5P10, 2.5 VA for protection c) LV side compartment : one no. ACB of 1600A, 50kA, 4Pole, Microprocessor based release with arrangement for bottom cable termination ( 100% for phase & 50% for N, Current density - 1A/ sq mm) The enclosure should be of IK10 type.The Enclosure shall construction shall be GI of thickness at least 1.6/2mm.The enclosure shall be Powder Coated. Each compartment will be provided with the door and pad locking arrangement. The Compartment illumination lamp with door operated switch shall be provided for each compartment. The Transformer compartment will have IP-34 ingress protection, whereas the HT/LT compartment will have IP-54 protection.The connection between HT and Transformer shall be by 3 runs of single core 95 sq mm XLPE aluminium cable and between Transformer to LT switchgear shall be appropriate rating Aluminium PVC sleeved Busbar | No.
C | Providing and erecting ISI Marked 3core 240 Sq.mm XLPE insulated 11 KV armoured cable Aluminium conductor IS-7098 to be laid on wall with clamps or in provided cable trench / pipe approved manner as directed. | m
D | Supplying and making cable end terminations for the following size of 11 KV grade, XLPE aluminium conductor armored cable including termination kit complete heat shrinkable sleeve etc. 3 C x 240 sq.mm 11 KV XLPE cable (Outdoor) | No.
E | SITC of following 1100 volts grade PVC insulated sheathed copper conductor armored control cables in existing trenches cables trays, clamped on wall with suitable saddles, fixing bolts, including testing and commissioning. 12 Core 4.0 sq mm PVC insulated copper conductor armored control cables | m
F | SITC of Cable end termination of the following PVC insulated sheathed aluminium conductor armored cables of 1100 volt grade including supplying and fixing of crimping lugs. Double compression glands with earthing provision and cable sockets 12 Core 4.0 sq.mm Control cable | No.
G | D.G. Set Supplying and erecting, commissioning and testing of Diesel Generating set confirming to IS: 4722:1968 & BS:5514 having continuous rating, 3 phase, 415 volts, 50 cycles A.C. supply comprising of a totally enclosed air/water cooled diesel engine with multi-cylinders developing suitable BHP not less than following capacity at 1500 RPM with 10% overload for one hour in 24 hours with standard accessories like fly wheel, lubricating oil cooler, "A" class governor, heavy duty fuel wheel and lubricating oil filter, oil bath air filler, lubricating oil pressure gauge, end exhaust manifold, standard set of tools with adjustable spanners, screw drivers, cylinder head to cover, joint cylinder head to exhaust, element lube oil filter, 12 / 24 volts electric starting equipment complete with standard heavy duty battery, dynamo, cut-outs, ammeter, necessary wiring, pressure gauge, starter etc and heavy duty Residential type exhaust silencer (With DEF System) and vertical hot air duct both | Ea
C/F
B/F
logged with asbestos rope, save oil trays, exhaust piping of required length, standard wall/floor mounted fuel with level indicator and piping and drip proof alternator, self excited, self regulated, screen protected, with excitation system, capable of delivering the rated system output at 415 volts, 3 phase, 0.8 PF, 50 Hz, 4 wire, running at 1500 RPM, conforming to IS-4722- 1968 with voltage regulation +/- 5% of rated voltage from no load to full load. Both the engine and alternator fitted on a common fabricated steel base plate with antivibration mounting engine and alternator both connected to each other by flexible flange coupling and with floor/wall mounted control panel box comprising of voltmeter ammeter, selector switches, ACB / MCCB / MCB of adequate capacity,
indicator lamps duly wired with HRC fuses. The alternator & control panel shall be connected with provided suitable capacity armoured cable and complete with Acoustic enclosure (canopy) made out of 16 SWG CRCA Sheet, sound absorbing material Rockwool of 64 density & 100 mm thick conforming to IS:8183 / PU Foam of 40 Density - at least 40 mm. The resin bonded rockwool covered from inside the canopy by perforated sheet with 3/4 mm holes, sound level not more than 75 dB at a distance of 1 mtr, as per PVCT norms.DG set should have in built fuel tank capacity of minimum 8 hrs of continous running capacity on full load . Erection, commissioning and satisfactory testing as per requirement with first filling of fuel (minimum up to the 80% of fuel tank capacity), oil, etc. with guarantee / Warrantee of complete system for Two years. & with obtaining all necessary certificate from Electrical Inspector. The Capacity and Ratings of DG sets are as below. (As per new CPCB4+ Emission norms Engine With - Turbo Charger, EGR (Exhaust Gas Recirculation), CRS (Common Rail Fuel System), DOC (Diesel Oxidation Catalyst), SCR (Selective Catalytic Reduction), Integrated wiring harness connected to ECU .) (R) Continuous rating of 750 KVA
A | AMF panel Providing & erecting approved make AMF control panel suitable for following size of 3 phase, 415 V., 50 cycles, A.C. diesel generating set complete of scope as detailed below: 1) Power module: A pair of electromechanically interlocked contactors (for mains & generator) Overload relay for generator contactor Neutral contactor for mains and generator Power socket for connections. 2) Control and metering module: Line voltage monitor. Generator voltage monitor Ammeter 3 items attempt start facility. Air circuit breakers/MCB/MCCB of suitable rating for auto/manual operation. Auto/manual switch. Emergency stop push buttons. Manual start push button. frequency meter. Engine hour meter. Two earthing studs. 3) Protection module: The engine shutdown in the unlikely event of Low lube oil pressure High cylinder head temperature. V belt failure. 4) Indicators with alarm Load on generator. 5) Indicators Load on mains Engine fails to start . Emergency stop battery charger. The AMF Panel of following capacity (D) AMF Control Panel for750 KVA3 phase DG Set | No.
B | UPS Supplying and erecting approved make online Un-interruptible Power Supply system comprising flat cum-boost charger with IGBT base rectifier & Inverter & sealed maintenance free SMF batteries. The charger having operating capacity for input 160-270V AC & inverter having output 230V,50 Hz Ac with 0.8 load power factor with battery, over/under voltage output with over load & short circuit protection equipment. The system housed in CRC sheet duly powder coated paint with following power backup.with MS painted batteries stand, 10% Overload capacity for momentary load. (J) 20 KVA 3 - phase with 1Hr Backup | No.
C | Lightning Arrestor SITC of Vertical Air Termination Solid aluminium with Base- 10 mm dia and 1000 mm long. Air Termination Base tested for conditioning, Ageing Test & Lightning impulse current withstand test: 100 kA of 10/350µs waveform in an accredited Third party laboratory as per 6.3 & 6.4 of IEC 62561-1 2017 protocol with MAST 34mm dia 3000 mm long- Cold Galvanized | No.
C/F
B/F
A | SITC of 8 mm dia solid Aluminium Conductor for roof top mesh grid and tested as per IEC 62561- 2 conducted in the Govt. accredited thirty party laboratory to meet the requirement of IS/IEC 62305 with Required Accessories - Aluminium Holding clamp at every 1 mtr distance, Aluminium/SS cross splicer at every crossing of Alu. conductor, Expansion piece with connectors at every 20 mtr distance, Aluminium straight Splicer to connect conductors. All Accessories should be tested as per IEC 62561-1 2018 Cl. 6.3 for conditioning & Ageing Test & 6.4 for Lightning impulse current withstand test: 100 kA of 10/350µs waveform(Ageing & Electrical test ) conducted in a sequence manner & tested in the Govt. accredited Third party laboratory to meet the requirements of IS/IEC 6230 | m
B | SITC of 10 mm MS Round Solid Conductor having smooth surface Should be tested and use exclusively for lightning protection (Vertical Riser/Down Conductor which shall be concealed in Column OR Flushed on) to meet the requirement of IS IEC 62305 With Accessories - Earthing stud of dimension SS-75mm OD plate with 10mm dia tail connector used in structural steel ring earthing system to meet the requirements of IS/IEC 62305. (For Interconnecting the Column and the Terrace AL Conductor / Strip/Flat), SS Cross Connector to connect Earth fixing point to vertical raiser/Down conductor, SS Straight Splicer at every 4 Mtr to connect MS conductor in column, Bonding /Rebar Clamp at every 3 mtr suitable for interconnecting round conductor with reinforcement inside the concrete for structural earthing system, SS connector -To connect external conductor 8- 10 mm with earth fixing point. All Accessories should be tested as per IEC 62561-1 2018 Cl. 6.3 for conditioning & Ageing Test & 6.4 for Lightning impulse current withstand test: 100 kA of 10/350µs waveform(Ageing & Electrical test ) conducted in a sequence manner & tested in the Govt. accredited Third party laboratory to meet the requirements of IS/IEC 6230 | m
C | SITC of Galvanized Steel Flat 25x6 mm thickness from earth electrode directly in ground as required. Zinc coating: 500 g/m square (Approx:70 micron coating) tested and used exclusively for lightning protection earthing system and ring equipotential bonding. | m
D | SITC of 14.2 mm dia 3 mtr long Earth electrode of High tensile steel electrode with 250 micron copper bonding & 1 bag of Carbon fill Based environment friendly backfill tested as per IEC 62561-7 in NABL accredited Laboratory and suitable stainless Steel double sided clamp. Eco Friendly rust proof heavy duty weather proof Polyethylene Earth Pit Chamber with following dimensions :254 mm dia (top), 330 mm dia (bottom) & 260 mm (height). | No.
E | Earthing Supplying & erecting funnel type earthing having earth plate of following size burred in specifically prepared earth pit 3 mtr. below ground with 40 kg. charcoal and salt with alternate layers of charcoal & salt, 20mm.dia. G.I. pipe with Funnel with a wire mesh for watering & bricks masonry block, C.I. Cover complete as per para 7.3 of IS 3043 with necessary length of double Galvanised Iron / copper earth wire No 6 SWG bolted with lug to the plate and covered in 12 mm dia. G.I. pipe 2.5 mtr long complete connected to the nearest switch gear with end socket as per direction & duly tested by earth tester confirming to IS (As per drawing) with following specification (C) with 60 x 60x 0.315 cms. Copper earth Plate | No.
F | Supplying & erecting in earthpit of minimum bore dia. 225mm size approved make Safe Earthing Electrode consisting Pipe-in-Pipe Technology as per IS 3043-1987 made of corrosion free hot dipped G.I.Pipes having Outer pipe dia of 80 mm having 80-200 Micron galvanising, Inner pipe dia of 40 mm having 200-250 Micron galvanising, connection terminal dia of 14 mm with constant ohmic value surrounded by highly conductive compound with high charge dissipation suitable for following type of applications with chamber and heavy duty cover (A)(approved make OEM has to submit test certificate including value of earth resistance of installation duly stamped and signed by agency and officer Incharge has to ensure the value of earthing resistane mentioned in test Certificate) & having back filling compound of (B) Inner chemical (CCM Compound)- Resistivity:- 0.2 ohm / meter testing as per IEC 62561-2017, Voltage drop:- < 1 volt at no load & dry form, Sulphar content:- <2%(C) Back fill Compound :- Earthing compound should be capable to retain moisture for long time Necessary test report must be submitted by Agency. [C] For Electrical Installation covering Transformer Neutrals, Lightning arrester Earthing, A.C.Plant & Sensitive Computer System(like Automation, SCADA)i.e. independent Earthing located in other than normal soil i.e. Soft Rock, Marshy Soil etc.. -Length of Pipe : 3 Mtrs. -Back filling Compound :2 nos Bags of 25 Kg. | No.
C/F
B/F
A | Providing and erecting Pipe type earthing with 40 mm dia 2.5 mtr long 'B' grade G.I. pipe with necessary coupling buch buried in specially prepared earth pit & G.I. earth wire of 8 SWG erected & connected as directed (For panel) | No.
B | Earth wire/strips : Providing and erecting HOT deep Galvanised iron strip wire 8 to 16 SWG. | kg
C | Providing and erecting Annealed bare Copper wire 8 to 16 SWG. | kg
D | Providing and erecting required size HOT deep Galvanised iron strip for earthing of H.T. , OCB/ ACB/ Transformer LT panel board, Motors etc. using proper clamp. | kg
E | Providing and erecting required size Copper strip for earthing of H.T. OCB / ACB/ Transformer, LT panel board, Motors etc. using copper clamp. | kg
F | providing and erecting Mains with ISI marked, 1.5KV grade electrolyte multi stranded, annealed copper conductor with heat resistant PVC insulated conforms to IS 694, IEC - 227 erected in existing pipe of following size (Specifically for control panel, relays, power switchgears, motor starters & control wiring) with required size of copper lugs, nuts and bolts if required. (e) One wire 6.00 sq. mm | m
G | SITC of Water Tight Junction Box With necessary clamp for mounting of the J.B. ( All the cable / wire connections to the JB shall be with the Water tight Glands only ) | No.
H | Telephone Distribution Providing & erecting main Distribution (MDF) indoor type, back mounted frame as per DoT standard approved with krone strips (a) Suitable for 100 pair | No.
J | PVC Conduits Providing and erecting ISI mark Medium class RIGID PVC PIPES of following size complete to be erected on/in wall or ceiling erected with necessary PVC fittings & Junction boxes fixed with adhesive solution & Clamps with following dia of pipes, in approved manner as directed (b) 25 mm | m
K | Providing and erecting ISI mark Medium class RIGID PVC PIPES of following size complete to be erected on/in wall or ceiling erected with necessary PVC fittings & Junction boxes fixed with adhesive solution & Clamps with following dia of pipes, in approved manner as directed (d) 40 mm | m
L | Telephone Point Wiring Supplying & erecting approved make Telephone Cable electrolytic copper conductor PE insulation twisted in two pairs, & wrapped with FRLS PVC tape & sheathed with FRLS PVC or HFFR outer Jacket suitable for telephone wiring & confirming to C-DOT erected in existing pipe. of following size of conductors & nos.of pairs. With necessary connections. [A] Conductor Size 0.5 mm (a) Unarmoured (5) Ten Pairs | m
M | Supplying & erecting approved make LAN cable of following size in existing pipe as per direction [C] CAT - 6 | m
N | Telephone Outlet Point Providing following type of Modular Type Accessories mounted with PVC / metallic/Wooden box, single mounting base frame covered with textured / metallic/white front plate , modules erected with necessary connections as per site situation directed by Engineer In charge. (3) Two Pin/RJ-11 Telephone Socket [A] For One Gang. Cat.III | No.
c/f
b/f
A | Providing following type of Modular Type Accessories mounted with PVC / metallic/Wooden box, single mounting base frame covered with textured / metallic/white front plate , modules erected with necessary connections as per site situation directed by Engineer In charge. (8) Computer RJ-45 socket Cat.III | No.
B | SITC of 24 x 10/100/1000BASE-T ports 4 x Gigabit RJ45/SFP Combo ports Advanced L2 switching and security features L2+ Static Routing Optional “standard mode” or “surveillance mode” management user interface [Approved by Competent Authority i.e. not Below the rank of Executive Engineer ] | No.
C | SITC of Patch Panel Cat 6 UTP Keystone Type- 24 Port-Fully Loaded [Approved by Competent Authority i.e. not Below the rank of Executive Engineer ] | No.
D | SITC of CAT6 UTP 24AWG PATCH CORD:1M,Plug 30U' Snag less [Approved by Competent Authority i.e. not Below the rank of Executive Engineer ] | No.
E | Supply Installation Testing & Commissioning of 2MP IR Dome Camera(2.8mm Lens with Aperture of F1.6 (By Default)/F2.0(On demand)),Audio Support, 1/2.8” SONY - CMOS, 2MP, 0Lux with IR LED on, 2.8mm IR Distance up to 50m, Video Analytics: Trip Wire, Intrusion Detection and Motion Detection, H.265/H.264/M-JPEG Video Compression, PoE Support, NAS Storage, SD Card(512GB), Quad Stream Support, 1/1 Audio I/O, 1/1 Alarm I/O, True WDR, 3D Noise Reduction, Adaptive Streaming, Smart Streaming and ROI, SNR > 70 dB, ER Compliant & Cyber Secured as per ISO / IEC 27402, BIS, CE, FCC, RoHS, IK10, IP67, UL, NDAA Compliant & STQC Certified. | No.
F | Supply Installation Testing & Commissioning of 2MP IR Bullet Camera(6.0mm Lens with Aperture of F1.6(By Default) /F2.0 (On demand)),Audio Support, 1/2.8” SONY - CMOS, 2MP, 0Lux with IR LED on, 6.0mm, IR Distance up to 50m, Video Analytics: Trip Wire, Intrusion Detection and Motion Detection, H.265/H.264/M-JPEG Video Compression, PoE Support, NAS Storage, SD Card(512GB), Quad Stream Support, 1/1 Audio I/O, 1/1 Alarm I/O, True WDR, 3D Noise Reduction, Adaptive treaming, Smart Streaming and ROI, SNR > 70 dB, , BIS, CE, FCC, RoHS, IK10, IP67, UL, NDAA Compliant & STQC Certified. | No.
G | Supply, Installation, Testing & Commissioning of Outdoor 1/2.8 inch CMOS 2 MP or better, IR PTZ Camera, Effective pixels 1920 x 1080, 2MP 25x Optical Zoom & 16x Digital Zoom, tripple stream; IR distance: 100 meter; Max frame rate: 25 fps; Lens type: Wide 5 to 6mm, Tele 120 to -150mm Motorized Auto focus zoom lens; Memory card slot: Min 256GB support. Minimum Illumination- Sense up on- Color: 0.005 lux color, B/W: 0 lux IR On, WDR 120dB, Edge Video Analysis Video Motion Detection, Intrusion, Lioter, Counter & Tampering, 3DNR, BLC, HLC, White Balance, EIS, Defog, Mechanical switchable IR filter (Auto ICR), Pan Range 360° continuous, Tilt Range -10° to 90°, Pan/Tilt Modes - Pan: 0.1°/s - 180°/s; Tilt: 0.1°/s - 90°/s, Presets 256, Preset Accuracy 0.25 Deg, 16 Patrol & Tours, Alarm I/O - 1In/1Out, 2-Way Audio- 1/1 Channel In/Out, 256GB Memory card slot, 4 individually configurable privacy masks, 8 Region of Interest, POE+ (802.3 at) or 24VAC 3A for indoor/Outdoor application, IP66/67, IK 10 , ONVIF Profiles S/G/T, Certifications: ONVIF Profile S/G/T compliant, UL/CSA 62368-1, CE (EN 50130-4), FCC Part 15, EN 55032, NDAA & RoHS (EN63000) compliant. Allong with power supply and Mounting kit. | No.
C/F
B/F
A | Supply, Installation, Testing & Commissioning of Video Management Software supporting ONVIF Profile S & G (Listed on ONVIF website), PSIA, Real time streaming protocol (RTSP) standards, emerging technologies in the industry, like 4K resolution, H.265 video compression codec, 3D PTZ control, 360° Fisheye camera and multi-imager/lens camera support. Software proposed should be SQL based with at least 500 camera and 05 clients included to view/record all the cameras, licenses should expandable up to 1000 cameras & 10 clients without any additional version upgrade. N+1 redundancy should be supported with proposed VMS. Vendor to consider and quote all necessary additional software, Licenses and accessories required to make the system functional. Video Management Software shall support - 1) Perpetual software licence; must not be renewed periodically. 2) 2000 cameras management on single server instance. 3) N:1 and N:M recorder redundancy; application should also be able define priorities among the redundant servers 4) Digital Signature and password protection on exported clips 5) Calendar Search with thumbnail image preview of recording and quick export of video clips 6) Smart Motion Detection/Search on recorded video for multiple regions of interest 7) Tracking object from selected set of interlinked surrounding cameras with smart algorithm (with min. 12 cameras) 8) Export recording by creating a package of clips of multiple cameras at different times that can be played sequentially 9) Centralized Device Maintenance: Tool to perform bulk camera firmware and password updates. Software OEM should have toll free number for technical or service support. | No.
B | Supply Installation Testing & Commissioning of Recording Server / Network Storage Manager (NSM) supporting ONVIF Profile S & G, PSIA, real time streaming protocol (RTSP) standards, emerging technologies in the industry, like 4K resolution, H.265 video compression codec. System proposed shall have scalability up-to 128 cameras per recorder with sufficient licenses to record all the cameras in this requirement. It shall support simultaneous recording, live monitoring, playback/search of recorded video for all cameras supporting, support scheduled backfilling of the recordings from the edge storage/SD card of cameras for robust recording against temporary network failure. Recording to be considered for 30 days at full resolution, 25 FPS in RAID 5. Vendor to submit storage calculations. It shall have Intel® Xeon Silver 4210R 2.4G, Minimum 32GB RAM; Dual, Hot-plug, Redundant Power Supply (1+1), 750W; OS drive: 2 (240GB) x M.2 Sticks Protected by RAID 1; 12 field upgrade 4 TB or 8 TB or 10 TB or 12 TB or 16 TB SATA/SAS hard drive options, Data RAID Level: 0, 1, 5, 6, 10. Network: 4 x 1GbE supporting network throughput of 800 MBPS, Standard VGA/HDMI Graphics Adapter, Windows 10/Windows Server 2012/2016, Microsoft SQL Express 2019. Standard VGA Graphics Adapter, 3 USB; Certifications: UL, CE/EN, FCC, RoHS. | No.
C | Supply Installation Testing & Commissioning of 20TB Hard drive | No.
D | Supply of UHD LED Smart T.V. of 138.8 cm (55 inch), with Ultra HD (4K) (3840 x 2160), Viewing Angle - 178 degree, Aspect Ration - 16:09, Powr supply, 100-240 VAC 50-60 Hz, supporting smart features like Bluetooth, Built-in Wi-Fi, Screen Mirroring, 1 TV,Warranty Card, AC Power Cord, Remote Control, User Manual - 1 unit Each, Batteries - 2 Units, Speaker Output RMS 20watt, with 3 side HDMI port, 2 nos. UCS ports. | No.
E | Supply of 9U/600 Rack/ Welded/WM/Off White,Glass Door/9U/WM/Gray,Server /IT Rack mount power distribution unit, 1Ph, 230V, 16A, 50/60Hz, 2U standard with 6 X Indian Round Pin 5/15A, Inlet Plug type 16A Indian Round Pin, 16A MCB - PDU Rating 3.6KVA/Side feed-1.5Mt/ Black,Horz. Cable Organiser/1U/Loop,Cantilever Shelf/Type2/1U/Off White,Mounting Hardware-CR (Pack of 20),ITE / Server Rack Air Circulation module/90CFM | No.
F | SITC of 24 x 10/100/1000BASE-T PoE ports, 4 x Gigabit RJ45/SFP Combo ports, Advanced L2 switching and security features, L2+ Static Routing Optional “standard mode” or “surveillance mode” management user interface 193 W PoE budget, [Approved by Competent Authority i.e. not Below the rank of Executive Engineer ] | No.
G | SITC of Patch Panel Cat 6 UTP Keystone Type- 24 Port-Fully Loaded [Approved by Competent Authority i.e. not Below the rank of Executive Engineer ] | No.
H | SITC of CAT6 UTP 24AWG PATCH CORD:1M,Plug 30U' Snag less [Approved by Competent Authority i.e. not Below the rank of Executive Engineer ] | No.
J | SITC of LIU 12 PORT Rack Mount - Loaded (LC) SM [Approved by Competent Authority i.e. not Below the rank of Executive Engineer ] | No.
K | SITC of PIGTAIL LC SM SIMPLEX LENGTH- 1m [Approved by Competent Authority i.e. not Below the rank of Executive Engineer ] | No.
C/F
B/F
A | SITC of PATCH CORD LC-LC SM DUPLEX LENGTH- 3m [Approved by Competent Authority i.e. not Below the rank of Executive Engineer ] | No.
B | SITC of Face Plate - Single (Keystone Jack,square) [Approved by Competent Authority i.e. not Below the rank of Executive Engineer ] | No.
C | SITC of Jack Cat 6 Keystone UTP [Approved by Competent Authority i.e. not Below the rank of Executive Engineer ] | No.
D | SITC of Maximum distance of up to 10 km Hot-pluggable Single-mode fiber 1000BASE-LX (IEEE 802.3z standard) Duplex LC connector MSA, RoHS-compliant [Approved by Competent Authority i.e. not Below the rank of Executive Engineer ] | No.
E | SITC of 20 x SFP ports 4 x Combo 10/100/1000BASE-T/SFP ports 4 x 10G SFP+ ports 6 kV surge protection on all RJ-45 access ports Switch Resource Management (SRM) for ﬂexible management of system resources Redundant Power Supply (RPS) support MPLS L2VPM/L3 VPN support Full L3 routing protocol support including OSPF, BGP, and ISIS for IPv4/IPv6 SDN-enabled switch, compatible with Openflow 1.3 10-GbE SFP+ to SFP+ 1M Direct Attach Cable [Approved by Competent Authority i.e. not Below the rank of Executive Engineer ] | No.
F | Supply, Installation Testing & Commissioning 5 Mtr. HDMI Interface Cable as per the detailed Specifications supports transmission of 4K Signals as per the detailed Specifications | No.
G | Supply, Installation Testing & Commissioning 10 Mtr. HDMI Interface Cable as per the detailed Specifications supports transmission of 4K Signals as per the detailed Specifications | No.
H | Supply, Installation Testing & Commissioning 15 Mtr. HDMI Interface Cable as per the detailed Specifications supports transmission of 4K Signals as per the detailed Specifications | No.
J | Supplying & erecting approved make LAN cable of following size in existing pipe as per direction [C] CAT - 6 | m
K | Providing & Erecting 6 core fibre optic SM 9/125um double sheath, CSTA, Unitube, Outdoor cable (per m) | m
L | Fire Detection System Supply, Installation Testing & Commissioning of UL864, 10th Edition Microprocessor based 6 loop and expandable up to 10 Loop, True Peer-to-Peer Networkable Addressable Fire Alarm Control Panel with minimum 600 characters LCD display, 4000 event plus 1000 alarm log history events, QWERTY keypad for programming. The panel should be equipped with sufficient numbers of loops considering 20% spare capacity in each loop. Each loop shall have a capacity of minimum 318 analog addressable devices. The panel shall work in degrade mode in case of CPU failure, Products not having this feature may offer Redundant CPU. Four access levels, flash EPROM, 240 volts AC power supply, automatic battery charger, 24 volts sealed lead acid batteries sufficient for 24 hours normal working and 30 mins in alarm condition. The panel shall be compatible with Integrated 8 channel Digital Voice Evacuation System Controller capable of broadcasting Evacuation Messages on same peer-to-peer Network and 2 ways Communication Fire Fighters System capable of supervising all the speaker circuits with adequate zone control and accessories. Failure of Fire Panel CPU shall not result in failure of DVC operation. The Fire Fighters Telephone System shall be capable of having minimum 30 Telephones in conference in multiple FFT Risers. | No.
c/f
b/f
A | The mimic annunciator for the fire alarm control panels (FACP). This provides the FACP with remote, serially-connected display. A five inch touchscreen display provides system status, point information, and event counters. The display shows two events simultaneously, and pages through up to 50 of the highest priority events in the system. The RLD also provides system control with six programmable softtouch buttons as well as Acknowledge, Silence, Reset and Drill. | No.
B | Supply of UL268, 7th Edition Addressable Multi-criteria Photo-Thermal Detector with sensitivity range of 0.5 to 4.0% obs/ft.The intelligent multi criteria detection device shall include the ability to combine the signal of the thermal sensor with the signal of the photoelectric signal in an effort to react hastily in the event of a fire situation. It shall also include the inherent ability to distinguish between a fire condition and a false alarm condition by examining the characteristics of the thermal and smoke sensing chambers and comparing them to a database of actual fire and deceptive phenomena. The detector shall have twin bi-colour LED for 360 deg viewing. Addressing shall be with user friendly rotary decimal switches. | No.
C | Supply of UL Listed Addressable Rate of Rise Heat Detector rated at 8.3 deg C/min. The detector shall have twin bi-colour LED for 360 deg viewing. Addressing shall be with user friendly rotary decimal switches. | No.
D | Supply, Installation, Testing And Commissioning of UL listed Addressable Manual Call Point (Pull down / Break Glass Type). The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. | No.
E | Supply, Installation, Testing And Commissioning of UL Listed Sounder cum Strobe rated at 80 dBA @ 3m for Audible annunciation and 115cd flashintg at 1 Hz for visual indication. UL Listed | No.
F | Supply, Installation, Testing And Commissioning of Addressable Control Module for Sounders / Strobes / Sounder cum Strobes. The control module shall provide supervised NAC output rated at 24v DC, 2A. The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. Addressing shall be with user friendly rotary decimal switches. Module shall be supplied with mounting plate from OEM for ease of installation & maintenance. | No.
G | SITC of Optical Beam Detector with transmitter and receiver set of UL Listed. The detector shall have Minimum 90 m range, Automatic compensation, Maximum coverage 1500m2, Automatic Signal strength adjustment, Emitter unit can be powered directly from zone (or loop), Features a Latching or Non- Latching fault relay, Full line continuity options | No.
H | Supply, Installation, Testing And Commissioning of UL Listed Isolator Module for Isolating short / dewired / loose circuits with automatic resetting arrangement. Isolator Base can also be proposed, however in that case needs to be considered with each detector & module. The device shall have an LED which shall blink in normal state & get steady on activation to monitor the heath status of the device. Module shall be supplied with mounting plate from OEM for ease of installation & maintenance. | No.
J | Supply, installation, testing & Commissioning of Battery pack suitable for back up of 4 hours with charger in case of Alarm condition. | No.
K | Supply, installation, testing & Commissioning of response indicator | No.
L | Supply & laying of 2 Core X 1.5 sq.mm. FRLS Armoured PVC Insulated copper cable | m
c/f
b/f
A | Supply & laying of 4 Core X 1.5 sq.mm. FRLS Armoured PVC Insulated copper cable | m
B | ACCESS Control System Supply, Installation, Testing and Commissioning of standalone wire-free electronic access reader cum controller with wire-free door exit functionality and strengthen access via an electro-mechanical locking mechanism, supports RFID (MIFARE® DESFire® EV1/EV2/ EV3, MIFARE® Plus, MIFARE® Ultralight C, MIFARE® Classic) and Mobile credentials (Bluetooth Digital Key and Near Field Communication (NFC) capability). Compatible with communicating on the cloud as well as vicinity access management platform with data on card technology, Capable of securing data communication with AES 128 bit encryption over networked communication, Supports up to 40000 door opening on single battery cycle, Certified with CE, UKCA, ACMA, EAC, IMDA, NCC, BIS, Ü-Certificate, EN 1634-1 EI 60 with Electro-mechanical euro profile lock with projected latch and deadbolt. (axe distance 85mm). Steel mortise lock with reversible projection latch. The auxiliar latch (anticard) projects and deadlocks the latch and the lever retracts deadbolt and latch simultaneusly (panic function).Squared shape and deadbolt detector for privacy. | No.
C | Supply, Installation, Testing and Commissioning of electronic communicator supports POE (IEEE 802.3af) connectivity with a built-in tamper switch that communicates with 16 wire-free readers in the range of 10-12 meters, certified with CE, FCC/IC, RCM, SRRC, EAC | No.
D | Supply, Installation, Testing and Commissioning of electronic extender supports BUS485 connectivity with a built-in tamper switch that communicates with 16 wire-free readers in the range of 10-12 meters, certified with CE, FCC/IC, RCM, SRRC | No.
E | Supply, Installation, Testing and Commissioning of a web-based access control management tool that enables users to program access time zones, manage different calendars and view audit trails from each door. User-friendly interface and simple to set up and configure, giving users the flexibility and control as per requirement, supports multiworkstation compatibility with zero data corruption risk, data protection with SQL engine and Windows authentication, Supports 64000 doors, 4000000 users and unlimited access levels, compatible with property management systems, point of sale, standalone data on card technology, supports features like locker management, online monitorinng, lockdown, antipassback, event steam, roll call, card printing module, visitor management, partitions & locations, database syncronization, alarm & communications and many more secured with cybersecurity and BSI Kitemark Secure Digital Application with Mifare Programable 1K 150 units,secured enrollment unit supports RFID data assignment and encryption, Bluetooth and NFC technologies, Supports USB Type-B, 10BASE-T/100BASE-TX connectivity, certified with CE, FCC/IC, RCM,battery-operated programable device supports USB and RS232 connectivity, supports to initialise, diagnose, emergency opening, collect audit trails, update firmware for wire-free readers, certified with EN 55022 (1994), Class B, EN 50082 (1997) | No.
F | Supply, Installation, Testing and Comissioning of 2 Core 1.5 Sq MM Armourded Cable With Standard accessories | M
G | Supply, Installation, Testing and Commissioning of Multiple Credential, Face Recognition, QR/Barcode, MultiCLASS SE and Dual RFID (125kHz EM, HID Prox & 13.56Mhz MIFARE, MIFARE Plus, DESFire/EV1, FeliCa, iCLASS SE/SR/Seos, NFC), IP65, IK06, BLE | No.
H | Supply, Installation, Testing and Commissioning of BioStar 2 Time Attendance Standard Edition License Module (100~500 users) | No.
C/F
B/F
A | Supply, Installation, Testing and Commissioning of Workstation - Industry standard Intel based x64 platform computer system. Intel Core i7 12th generation 8C Processor, 32 GB of RAM DDR3/4, 512GB NVME SSD for Operating System, 1TB SATA Hard drive for application data, NVIDIA Quadro T400 4GB Graphics card, 1 x 1000Mbps ethernet network interface card along with appropriate licenced Operating System, licenced applications suites from OEM as per the technical requirement | No.
B | SITC of Turn Style / flap Gate with all kind of accessories and fixing | No.
Total Carried to Summary

## HVAC Work_BOQ
GOLDBOD NATIONAL ASSAY CENTER · HVAC BOQ — ALL-VRV SYSTEM (NO CHILLER)
SHEET 02 — HVAC, VENTILATION & FUME EXTRACTION — QUANTITIES & RATES
ITEM | DESCRIPTION | DIMENSION / DRAWING REF | L(m) | W(m) | H(m) | QTY | UNIT | RATE | AMOUNT
SECTION 1 — GROUND FLOOR: VRV SYSTEM [⭐ ALL VRV — NO CHILLER, NO CHILLED WATER PIPING]
A | VRV Outdoor Condensing Units — air-cooled, heat-recovery type (total GF installed 64TR) | GF design 55.8TR × 1.15 safety factor |  |  |  | 64 | No
B | VRV Ducted Indoor Units — labs, electrical room, storage, chemical store (concealed ceiling type) | Duct-concealed units for lab/store zones requiring ducted supply |  |  |  | 7 | No
C | VRV 4-Way Ceiling Cassette Units — office, reception, corridor, lobby zones | Cassette units for open/public GF zones |  |  |  | 8 | No
D | VRV High-Wall Split Units — Fire Assay labs (chemical-resistant coated coil, corrosion protected) | 3 Fire Assay rooms × 2 units each — corrosion-resistant coil coating |  |  |  | 6 | No
E | VRV Branch Selector Box / Refrigerant Distribution Box — GF zones | Refrigerant branch distribution — 6 zones GF |  |  |  | 6 | No
F | Outdoor condensing unit plinth + anti-vibration mounts (rooftop/ground) | Outdoor unit plinths — GF plant |  |  |  | 4 | No
G | Louvred screen (aluminium powder-coated) around outdoor units — GF plant area | Outdoor unit screening — GF |  |  |  | 2 | No
H | Refrigerant piping (liquid + suction) — insulated copper, outdoor to GF indoor units | Insulated copper ref pipe — GF runs (longer runs than FF due to lab spread) |  |  |  | 94 | m
J | Condensate drain pipes (PVC 25mm) — each GF indoor unit to drain | 26 units × 3.6m avg drop | 26 |  | 3.6 | 94 | m
SECTION TOTAL — GF VRV SYSTEM
SECTION 2 — GROUND FLOOR: TOILET & PANTRY EXTRACT VENTILATION
K | Centrifugal exhaust fans — GF toilets, pantry, WC, changing rooms (10 ACH extract) | GF: WC+Pantry+Changing |  |  |  | 3 | No
L | UPVC exhaust air ductwork — toilets to external discharge (150mm dia) | Toilet extract duct runs GF |  |  |  | 9 | m
M | Exhaust grille — stainless steel louvred (one per toilet/WC/pantry) | GF toilet/pantry exhaust grilles |  |  |  | 3 | No
N | Fresh air intake louvre + insect mesh — GF toilet areas | Fresh air replacement — GF |  |  |  | 4 | No
SECTION TOTAL — GF EXTRACT VENTILATION
SECTION 3 — FUME EXTRACTION + WET SCRUBBER SYSTEM [Independent of VRV — critical lab safety system]
A | Wet Chemical Scrubber Unit — acid/fume treatment before roof discharge (from drawing: SCRUBBER SPACE, left side) | Wet scrubber — PP/GRP construction, recirculating water, efficiency ≥98% |  |  |  | 1 | No
B | Laboratory Fume Cupboards — acid-resistant GRP/PP, ducted, face velocity ≥0.5m/s (Fire Assay + Wet Lab) | FA Parting+Wet Lab (3nos) + Cupellation/Fusion (3nos) = 6 total |  |  |  | 6 | No
C | Acid-resistant PP/PVDF roof exhaust fans — Fire Assay zones (20 ACH = 13848CMH) | Fire Assay × 2 labs + General Melting + Scrubber discharge — 4 fans |  |  |  | 4 | No
D | Acid-resistant UPVC fume duct (250mm dia) — hood to roof fan (Fire Assay labs) | Hood to roof fan runs — FA labs + melting hall |  |  |  | 120 | m
E | Chemical store extract fan (acid-resistant PP) + UPVC duct — Lab Store for Chemicals (15 ACH) | Chem store extract — 15 ACH, discharge via scrubber |  |  |  | 2 | No
F | Local Exhaust Ventilation (LEV) capture hoods — above furnaces + process workstations | Melting hall + weighing + observation + ICP workstations — 12 capture points |  |  |  | 12 | No
G | Scrubber recirculating pump + water treatment dosing unit + make-up water connection | Scrubber accessories — pump, dosing, level control |  |  |  | 1 | Item
H | Roof exhaust discharge stack — stainless steel, weather cap + bird screen (scrubber discharge) | Discharge stack above roof level |  |  |  | 1 | No
J | Fire dampers in fume duct penetrations (acid-resistant coated, UL listed) | Duct penetrations through fire-rated slabs/walls |  |  |  | 8 | No
SECTION TOTAL — FUME EXTRACTION + SCRUBBER
SECTION 4 — GROUND FLOOR: GI DUCTWORK — SUPPLY & RETURN (for VRV Ducted Units)
K | GI sheet supply air ductwork (insulated 25mm PIR) — GF ducted VRV unit distribution | GF floor area 736.3m² × 0.22 factor | 736.3 |  | 0.22 | 162 | m²
L | GI sheet return air ductwork (insulated) — GF ducted VRV return | GF area × 0.16 factor | 736.3 |  | 0.16 | 118 | m²
M | Flexible duct connections — ducted VRV unit to duct, diffuser last-metre drops (GF) | Ducted unit + diffuser flex connections GF |  |  |  | 29 | m
N | Duct insulation PIR 25mm — additional over exposed duct sections | Exposed duct extra insulation |  |  |  | 32 | m²
SECTION TOTAL — GF DUCTWORK
SECTION 5 — GROUND FLOOR: AIR DISTRIBUTION
P | Ceiling supply air diffusers 600×600 4-way (powder-coated steel) — GF ducted zones | GF active rooms × avg 2.5 diffusers/unit |  |  |  | 65 | No
Q | Return air grilles — wall-mounted steel louvred (GF) | GF return grilles |  |  |  | 39 | No
R | Motorised fire/smoke dampers UL listed — duct penetrations through fire walls (GF) | Fire wall/slab duct penetrations GF |  |  |  | 9 | No
SECTION TOTAL — GF AIR DISTRIBUTION
SECTION 6 — FIRST FLOOR: VRV CEILING CASSETTE SYSTEM
A | VRV Outdoor Condensing Units — air-cooled, heat-recovery type (31TR installed for FF) | FF design 26.6TR × 1.15 = 31TR installed |  |  |  | 31 | No.
B | VRV 4-Way Ceiling Cassette Units — all FF office/reception/service zones (17 nos from drawing) | Director+Meeting+CEO+Waiting+Workspace+Services+Apprentice+Cabins+Staff — 17 cassettes |  |  |  | 17 | No
C | VRV Branch Controller / Refrigerant Distribution Box — FF main branch | Refrigerant distribution — 3 branch controllers FF |  |  |  | 3 | No
D | Outdoor condensing unit plinth + anti-vibration mounts (rooftop) | Outdoor unit plinths — rooftop |  |  |  | 3 | No
E | Louvred screen (aluminium powder-coated) around outdoor units — rooftop | Outdoor unit screening |  |  |  | 2 | No
F | Refrigerant piping (liquid + suction) — insulated copper (outdoor to FF cassettes) | Insulated copper ref pipe — FF cassette runs |  |  |  | 60 | m
G | Condensate drain pipes (PVC 25mm) — each cassette to drain | 17 units × 3.3m avg drop | 17 |  | 3.3 | 56 | m
SECTION TOTAL — FF VRV CASSETTE SYSTEM
SECTION 7 — FIRST FLOOR: TOILET, WC & PANTRY EXTRACT VENTILATION
H | Centrifugal exhaust fans — FF WC Male, WC Female, CEO WC, Pantry (10 ACH) | FF: WC-M+WC-F+CEO-WC+Pantry |  |  |  | 4 | No
J | UPVC exhaust duct (150mm) — FF toilets to roof discharge | FF toilet extract duct to roof |  |  |  | 32 | m
K | Exhaust grilles SS louvred — FF toilet/pantry | FF extract grilles |  |  |  | 4 | No
SECTION TOTAL — FF EXTRACT VENTILATION
SECTION 8 — FIRST FLOOR: MINOR DUCTWORK & DISTRIBUTION (Cassette-Fed — No Central Duct Mains)
L | Flexible connections — cassette discharge to short duct run + diffuser drops (FF) | FF flex connections |  |  |  | 22 | m
M | Return air path — cassette return grille direct (no ducted return required for cassette system) | Return grille per cassette unit | 17 |  |  | 17 | No
N | Motorised fire/smoke dampers — FF duct penetrations | FF fire dampers |  |  |  | 14 | No
SECTION TOTAL — FF DISTRIBUTION
SECTION 9 — SECOND FLOOR: HVAC INFRASTRUCTURE (Future Expansion — VRV Provision)
P | Main supply air duct 900×200mm GI — SF future expansion (from SF drawing) | SF exp area 1039.8m² × 0.15 | 1040 |  | 0.15 | 156 | m
Q | Branch supply duct 300×60mm GI — SF future expansion | SF exp area × 0.25 factor | 1040 |  | 0.25 | 260 | m
R | Supply air diffuser 600×600 (blanked off, installed for future) — SF grid | SF exp area 1040m² ÷ 18m²/diff |  |  |  | 58 | No
S | Duct access panels + blank-off plates — SF supply points | One access panel per future supply point |  |  |  | 58 | No
T | VRV refrigerant pipe stubs — capped through SF slab (future cassette provision, replaces CHW stubs) | Capped ref pipe stub-outs SF — 8 nos |  |  |  | 8 | No
U | SF Washroom extract fan + UPVC duct (10 ACH) | SF washroom extract |  |  |  | 1 | No
V | SF WC extract fans × 2 | SF WC-1 + WC-2 extract fans |  |  |  | 2 | No
SECTION TOTAL — SF INFRASTRUCTURE
SECTION 10 — CONTROLS, BMS & AIR QUALITY MONITORING
A | VRV Central Remote Controller — group control per zone (GF + FF) | Zone group controllers — GF (5) + FF (3) |  |  |  | 8 | No
B | Digital room thermostat/controller — all occupied rooms (programmable, LCD) | GF+FF all active rooms — 30 nos |  |  |  | 30 | No
C | Lab differential pressure controller + display — all GF lab zones (neg pressure monitoring) | Lab zones requiring negative pressure — 6 rooms |  |  |  | 6 | No
D | CO₂ / air quality sensors — high-occupancy FF zones | Demand-controlled ventilation — FF high-occ zones |  |  |  | 5 | No
E | Temperature + humidity sensors — lab zones (±1°C critical control) | T+RH sensor per lab room for precision control |  |  |  | 6 | No
F | BMS (Building Management System) — HVAC integration module (VRV, fans, alarms) | Full BMS HVAC integration — VRV central monitoring + scheduling |  |  |  | 1 | Item
G | HVAC dedicated distribution boards — GF DB + FF DB (2 nos) | Dedicated HVAC electrical DB — 1 per floor |  |  |  | 2 | No
H | Power cabling from HVAC DB to each VRV unit — armoured cable | GF+FF power cable runs |  |  |  | 153 | m
J | Fume extraction control panel — scrubber system + lab extract fans (dedicated panel GF) | Scrubber + extract fan control panel + interlocks |  |  |  | 1 | No
SECTION TOTAL — CONTROLS & BMS
SECTION 11 — TESTING, BALANCING & COMMISSIONING (TAB)
K | Air balancing & testing report (TAB) — all supply/extract systems (ASHRAE 111 standard) | Full TAB — 95TR installed capacity |  |  |  | 95 | No.
L | VRV system commissioning — factory-trained engineer, full test run, warranty activation (GF+FF) | Complete VRV commissioning — all outdoor + indoor units |  |  |  | 1 | Item
M | Lab negative pressure verification — differential pressure test all GF lab rooms | Pressure test all lab zones — documentation for regulatory approval |  |  |  | 1 | Item
N | Fume hood face velocity test — 6 fume cupboards (≥0.5 m/s face velocity required) | 6 fume cupboards — individual velocity test + cert |  |  |  | 6 | No
P | Scrubber system commissioning + performance test (fume removal efficiency ≥98%) | Wet scrubber commissioning + efficiency cert |  |  |  | 1 | Item
Q | As-built drawings (CAD), O&M manuals, BMS handover + 2-day operator training | Full documentation + training package |  |  |  | 1 | Item
SECTION TOTAL — TESTING & COMMISSIONING
SUMMARY
SECTION TOTAL — GF VRV SYSTEM
SECTION TOTAL — GF EXTRACT VENTILATION
SECTION TOTAL — FUME EXTRACTION + SCRUBBER
SECTION TOTAL — GF DUCTWORK
SECTION TOTAL — GF AIR DISTRIBUTION
SECTION TOTAL — FF VRV CASSETTE SYSTEM
SECTION TOTAL — FF EXTRACT VENTILATION
SECTION TOTAL — FF DISTRIBUTION
SECTION TOTAL — SF INFRASTRUCTURE
SECTION TOTAL — CONTROLS & BMS
SECTION TOTAL — TESTING & COMMISSIONING
TOTAL — HVAC, VENTILATION & FUME EXTRACTION (ALL-VRV SYSTEM)

## Plumbing_Boq
GOLDBOD NATIONAL ASSAY CENTER ·
Plumbing WORKS
ITEM | DESCRIPTION |  | UNIT | QTY. | Supply Rates | ITC Rates | RATE | AMOUNT
SANITARY FIXTURES & CP FITTINGS:
A | Supply, Fixing, Testing and Commissioning of wall hung type white vitreous China European water closet (Approved Make and Model ) with concealed `P' or ‘S’ trap, Soft close seat and cover (heavy duty) C.P. brass hinges, including C.I. chair, with chair grouting, rubber buffers, C.P. nuts, bolts, etc. including accessories straight / offset type flexible single body push fit type WC pan connector , CI / MS brackets painted with two coats of approved shade over a coat of primer, C.P. Brass screws and wooden cleats. | 1 | No. | 15
B | Supply, Fixing, Testing and Commissioning of Concealed flushing cistern with or without Frame (Approve Make and Model ) with dual flushing actuator plate, flush stop function noise less float valve and fast filling action with all component parts of high quality complete in all respects. Rates to be included considering chasing in the wall as required and making good the same with appropriate mortar. | 1 | No. | 15
C | Supply, Fixing, Testing and Commissioning C.P. brass health faucet (Approved Make and Model ) assembly comprising hand held shower with 8 mm dia flexible tube with mounting bracket fixed on wall complete. | 1 | No. | 15
D | Supply, Fixing, Testing and Commissioning of CP brass Two way bib cock (Approved Make and Model ) including, necessary flange. | 1 | No. | 15
E | Supply and Fixing of C.P. Brass Double Coat Hook (Approved Make and Model ) fixed into wall with C.P.brass screws and rawl plugs etc. complete including cutting and making good the walls etc. | 1 | No. | 15
F | Supply, Fixing, Testing and Commissioning of stainless steel toilet paper holder (Approved Make and Model ). Including chasing in the masonary/R.C.C wall and making good with cement mortar. | 1 | No. | 15
G | Hadicapped toilet & shower (Approved Make and Model ) Supply, fixing, testing & commissioning of handicapped toilet with all require accessories. Designed for people with special needs. One set crane consists of following: EWC with flush tank & seat cover, wash basin, Pillar cock, Disable shower folding seat wall mounted grab bars for EWC, U shaped Grab Bar. With all required accessories with necessary holes and grooves work and making it well finished etc. Complete as per drawing and details. The quoted rated shall be including fixing of ewc, cistern, seat cover, internal fitting, wash basin (Wash basin to be installed with all required materials like bottle trap, waist coupling etc), lever faucet, grab bars, hand rail, pillar cock, angle cock, flexible pipe, connector pipe, bracket etc with required cement ( white/grey) with required tools, tackles, materials to complete the work up to satisfaction of E-I-C. | 1 | Item
| C/F | [6 empty] | 0
| B/F | [6 empty] | 0
A | Supply, Fixing, Testing and Commissioning vitreous China Wash basin (under / over the counter / Semi recessed) with below mention Accessories (Approved Make and Model ) 32 mm dia C.P brass waste coupling, 32 mm dia C.P cast brass bottle trap with union, 32 mm dia C.P brass pipe to wall & CP wall flange, rubber acceptors for waste connection and C.I. painted brackets bolts, nuts etc. (Cutting, finishing, making holes in Stone/wood shall be in civil / Interior contractor's scope). | 1 | No. | 17
B | Supply, Fixing, Testing and Commissioning of Wall / Table mounted automatic sensor / Manuel C.P. Brass single lever basin mixer/ Pillar cock with ss flexible connection and brass nuts complete. (Approved Make and Model ) In case of fixing in stone, Hole making / cutting will be done by civil / Interior contractor. However, marking of hole for fixing of pillar tap to be given by plumbing contractor according to selection of wash basin, pillar cock as per architecture / interior drawing. | 1 | No. | 17
C | Supply, Fixing, Testing and Commissioning of Stainless steel Kitchen Sink (Approved Make and Model ) with CI bracket (painted), 40 mm dia C.P. brass waste coupling, C.P. brass chain and rubber, 40 mm dia caste brass bottle trap with necessary union, C.P. pipe to wall & CP wall flange complete. In case of fixing in stone, Hole making / cutting will be done civil / Interior contractor. However, marking of hole for fixing of pillar tap to be given by plumbing contractor according to selection of wash basin, pillar cock as per architecture / interior drawing. | 1
| Single bowl without drain board. (SINK SIZE ) |  | No. | 2
D | Supply, Fixing, Testing and Commissioning of C.P. Brass Sink Mixer (Approved Make and Model ) swinging costed spout single hole tap with required size. In case of fixing in stone, will be fixed by civil / Interior contractor. However, marking of hole for fixing of pillar tap to be given by plumbing contractor according to selection of wash basin, pillar cock as per architecture / interior drawing. | 1 | No. | 2
E | Supply, Fixing, Testing and Commissioning of 15 mm dia C. P. Brass angle valve (Approved Make and Model )with C.P. brass flange. | 1 | No. | 19
C/F
B/F
A | Supply, Fixing, Testing and Commissioning of CP brass short body bib cock (Approved Make and Model ) including, necessary flange. | 1 | Item
B | Supply, Fixing, Testing and Commissioning of CP brass long body bib cock (Approved Make and Model ) including, necessary flange. | 1 | Item
C | Supply, Fixing, Testing and Commissioning of CP brass Towel Ring (Approved Make and Model ) with screw and rawal plug etc. | 1 | No. | 10
D | Supply, installation, testing and commissioning of Wall Mounted (Automatic Infra-Red Sensor based / Manuel) Liquid Soap Dispenser (Approved Make and Model ) , Power – Electrical (AC 220V/50Hz), Material – Brass, Finish – Chrome-plated, Capacity – 1000 ML, Made in India complete in all respect as per direction of the engineer-in-charge. | 1 | No. | 17
E | Supply, Fixing, Testing and Commissioning of wall mounted SS hand drier of (Approved Make and Model ) having twin blower integrated with timer and Touch-Free Infra-Red sensing system automatic which can work 230 volts single phase etc. complete in all respects as per direction of the engineer-in-charge. | 1 | No. | 9
F | Supply, installation, testing, and commissioning of Paper Dispenser (Approved Make and Model ) Construction : SS- 304, Operation : Manual, Application : Wash basin Area, Capacity : 200 C-Fold/ Multifold, complete in all respect as per direction of the engineer-in-charge. | 1 | No. | 9
G | Supplying and erecting of (Approved Make and Model ) horizontal / vertical mounting (Floor / Wall mounted ) type storage Water heater (Geyser) with copper container housed in M.S./S.S./ABS body insulated with glass wool/puff complete with heating elements, adjustable thermostats 30ºC to 85ºC, indicating lamp, safety valve, fusible plug, etc. Complete erected with coach bolts, nuts. washers, Including inlet outlet flexible braided hose pipe, telfon tape, flanges etc complete.. Voltage / Frequency (V/Hz) : 230V / 50Hz | 1
| 10 Ltrs |  | Item
H | Supply, Fixing, Testing and Commissioning of white glazed vitreous China large flat back lipped front Urinal basin (Approved Make and Model ) with below mention Accessories C.I bracket (colour painted) 40 mm CP brass domical waste, 40 mm C.P. caste brass bottle trap, CP flush pipe with spreader & other necessary fittings C.P. brass hex nipple; elbow; unions, washers, cap, C.P. nuts, bolts etc. | 1 | No. | 7
J | Supply, Fixing, Testing and Commissioning of Infra-Red based Electronic Urinal flushing system (Approved Make and Model ) operated on 6V DC (4AA) battery for urinals comprising of solenoid valve, concealed built in strainer & flow mechanism piping, flush mounted sensors with all accessories & fittings complete in all respect in fully operational condition etc including cutting and making good the wall where required. | 1 | No. | 7
C/F
B/F
A | Supply and Fixing of white glazed vitreous China urinal partitions of approved make including Rawl plugs, screws or any other approved device for Fixing arrangements. | 1 | No. | 7
B | Providing and fixing Heavy class SS grating with Collar 150 x 150 mm (cockroach trap) with Approved Make and Model, including setting in floor with cement mortar to match with floor finish as per architect requirements. | 1 | No. | 24
C | Providing and fixing Heavy class SS single piece grating 150 x 150 mm size of (Approved Make and Model ), including setting in floor with cement mortar to match with floor finish as per architect requirements. | 1 | Item | Item
D | Supply of 15 mm dia CP brass extension nipple / hex nipple up to 50 mm long complete in all respect. (This item shall be operated only In case of material supplied by contractor, No labour charges shall be paid) | 1 | Item
TOTAL OF SECTION-A SANITARY FIXTURES & CP FITTINGS CARRIED OVER TO SUMMARY
WATER SUPPLY :
WATER SUPPLY (INTERNAL & EXTERNAL) :
CPVC Pipe Internal :
A | Providing and fixing, to wall, ceiling and floor, approved make, CPVC SDR 11 pipes and fittings, conforming to ASTM D 2846, for sizes up to 50 mm and Sch 80 piping for sizes above 50 mm confirming to ASTM F441, for hot and cold water supplies for all internals including jointing with CPVC solvent cement as per manufacturer recommendation ensuring airtight joints, with necessary specials, couplers, unions, elbow, equal tees, adapter (both male and female), reducer (single stage, double stage and triple stage), end cap, fabricated bend, etc., All termination points shall have Brass inserts fittings including testing, cutting and chasing in wall and floors with diamond cutter & making good the same by using 1:1 cement mortar over the fibber mesh / Chicken mesh, ceiling and floor etc. complete of the following nominal pipe size: | 1
Galvanised rubber sleeved clamps/ u bolts, brackets (External Pipe to be fixed with zinc coated clamp, Brackets and U Bolts etc ), passivated fasteners & direction arrows and Symbols of appropriate size and spacing as directed by E-I-C shall be included in the price
| 20 mm (NB) |  | m | 185
| 25 mm (NB) |  | m | 246
CPVC Pipe External (For Shaft, Terrace, Basement) :
B | Providing and fixing, to wall, ceiling and floor, approved make, CPVC SDR 11 pipes and fittings, conforming to ASTM D 2846, for sizes up to 50 mm and Sch 80 piping for sizes above 50 mm confirming to ASTM F441, for hot and cold water supplies for all internals including jointing with CPVC solvent cement as per manufacturer recommendation ensuring airtight joints, with necessary specials, couplers, unions, elbow, equal tees, adapter (both male and female), reducer (single stage, double stage and triple stage), end cap, fabricated bend, etc., All termination points shall have Brass inserts fittings including testing, cutting and chasing in wall and floors with diamond cutter & making good the same by using 1:1 cement mortar over the fibber mesh/ Chicken mesh, ceiling and floor etc. complete of the following nominal pipe size: | 1
Galvanised rubber sleeved clamps/ u bolts, brackets (External Pipe to be fixed with zinc coated clamp, Brackets and U Bolts etc ), passivated fasteners & direction arrows and Symbols of appropriate size and spacing as directed by E-I-C shall be included in the price
| 25 mm (NB) |  | m | 13
| 40 mm (NB) |  | m | 65
| 50 mm (NB) |  | m | 89
Thermal Insulation on Embedded in Wall
C | Providing & fixing thermal insulation of nitrile rubber (Class "O") of approved make on hot water pipes. Size of insulation tube to be matched / suitable to pipe size. (Density : 40–70 kg/m3 and Conductivity : 0.033 w/m) (wrapping of polyglass/other tape to protect insulation shall be paid separately) | 1
| 15mm (OD) [6mm thick insulation] |  | Item
| 20mm (OD) [6mm thick insulation] |  | Item
| 25 mm (OD) [6mm thick insulation] |  | Item
c/f
b/f
A | Providing, fixing, testing and commissioning of full way lever operated forged brass ball valve of brass body with forged brass hard chrome-plated steel ball working pressure not less than 10 Kg / sqcm with threaded / flanged joints complete with nuts, bolts, gaskets, washers etc. | 1
| 15 mm dia |  | Item
| 20 mm dia |  | Item
| 25 mm dia |  | No. | 2
| 32 mm dia |  | Item
| 40 mm dia |  | No. | 3
| 50 mm dia |  | Item
B | Supply, Installing, testing and commissioning C.I butterfly valve (Lever operated), wafer end type class PN 16 as per I.S:13095 or BS:5155, including providing of necessary flanges, nuts & bolts (GI), gaskets etc., complete (including cost of flanges) as per drawings, specification and as directed by the Engineer's Representative. | 1
| 50 mm dia |  | Item
| 65 mm dia |  | Item
| 80 mm dia |  | Item
| 100 mm dia |  | Item
| 150 mm dia |  | Item
C | Supply, installation, testing and commissioning of Auto Air Release Valve with isolation ball valve of 25mm NB as per IS 14845 with screwed ends suitable for working pressure of 10kg. Body shall be of Cast iron, seat ring shall be of EPDM rubber & orifice shall be LTB or SS. Vendor to include in his cost all fittings, accessories & consumables required for the satisfactory installation & working of the valve. | 1
| 25 mm dia |  | No. | 1
D | Supplying and fixing Prayag make High Pressure rated PVC ball float valve with and brass rods of required length suitable for Test pressure of not less than 10 kg/sq cm. of the following sizes. | 1
| 50 mm dia |  | No. | 1
E | Providing and fixing CI Dual plate wafer type non return valve / check valve [PN 16] With SS-304 Discs and Nitrile Rubber Lining with Bronze Disc, Seat Test Pressure 16 Kg/cm2g tested to 24 Kg/Sq.cm pressure complete with all fitting and accessories i.e. rubber gasket, flanges, union, nuts, bolts, washer etc. | 1
| 40 mm dia |  | Item
| 50 mm dia |  | Item
| 65 mm dia |  | Item
| 80 mm dia |  | Item
F | Providing, fixing, jointing and testing, PN-10 pressure rating heavy quality Brass multi utility non return valve / Check valve confirming to IS 778, with screwed end, Test Pressure : Shell : 15 kg/cm², Seat : 10 kg/cm² on water supply lines of the following nominal bore (NB) size: | 1
| 40 mm |  | Item
| 50 mm |  | Item
| C/F | [6 empty] | 0
| B/F | [6 empty] | 0
A | Supplying fixing, Testing and commissioning Water meter with direct reading Dial in KL with all integral parts of Gun metal / brass up to 50mm dia. And C.I body above 50mm dia. with necessary fitting such as Threaded Pieces, union pressure gauge and isolation cock, flange piece for future removal, flanges/union complete for following size pipe line (1 No. strainer , 3 Nos. valves & 2 Nos. Pressure gauge shall be provided at inlet & outlet and cost shall be inclusive for the same). Ball valve up to 50mm dia and Butterfly valve above 50mm dia to be considered. | 1
| 50 mm dia |  | Item
| 65 mm dia |  | Item
| 80 mm dia |  | Item
B | Supply, Installation, Testing and commissioning of Water hammer arrestor, hydro pneumatic air cushion and 'O' ring sealed pistons fixed screwed with unions and fixing accessories, nuts, bolts, gaskets, washers, supports etc., matching flanges to suit the piping material specified and in accordance with specification. | 1
| 25 mm dia |  | No. | 1
C | Construction brick masonry chamber (for Housing valves & accessories) Valve chamber with 75 class designation brick work in cement mortar 1:5 (1 cement : 5 find sand) for valve, with cover fixed in cement concrete slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) necessary excavation foundation concrete 1:5:10 (1 cement : 5 fine sand : 10 graded stone aggregate 40mm nominal size) and inside plastering with cement mortar 1:3 (1 cement : 3 coarse sand) 12 mm thick finished with a floating coat of neat cement complete as per standard design. ( Rate to be quoted considering clear size of chambers) | 1
| 1200mm x 900mm x up to 1000 mm depth with 600x600 mm size FRP Cover and frame of load bearing capacity of 12.5T fixed in cement. |  | Item
TOTAL OF SECTION-B WATER SUPPLY (INTERNAL & EXTERNAL) CARRIED OVER TO SUMMARY
INTERNAL & EXTERNAL SEWAGE/DRAINAGE NETWORK:
A | Supply, installation, testing and commissioning UPVC pressure pipes of 6Kg/Sq.cm² pressure rating class III (IS : 4985-2000) including fittings like tees, bends, "Y", cowl, cleanout plug, reducers, bushings, coupling including clamping and supporting as per specifications, jointing with solvent joint, testing etc. complete as directed. Note : 1.0 Only Moulded fittings shall be used for all size pipe dia , No fabricated fitting allowed . 2.0 Rigid fabricated MS hot dip galvanized/ painted with 2 coats of synthetic enamel paint over one coat of zinc chromate primer to be provided as per dwg. for pipe sizes 200mm & above. 2.For all shaft every floor shaft signages mention with direction of flow indication. 3.For all basement level every 20mtr and at terrace level every 10mtr flow direction of pipe with type of pipes to be mentioned by vendor as per direction of site in charge. (For Terrace , building and basement Suspended lines) | 1
Galvanised rubber sleeved clamps/ u bolts, brackets (External Pipe to be fixed with zinc coated clamp, Brackets and U Bolts etc ), passivated fasteners & direction arrows and legend boards of appropriate size and spacing as directed by E-I-C shall be included in the price
Cutting and chasing in wall and floors with diamond cutter for UPVC pipes and fittings and making good the same by using 1:1 cement mortar over the mesh.
| 40 mm |  | Item
| 50 mm |  | m | 29
| 75 mm |  | Item
| 110 mm |  | m | 296
| 160 mm |  | m | 38
| 200 mm |  | m | 207
| 250 mm |  | Item
| 300mm |  | Item
B | Supply, installation, testing and commissioning UPVC pressure pipes of 10 Kg/Sq.cm² pressure rating class V (IS : 4985-2000) including fittings like tees, bends, "Y", cowl, cleanout plug, reducers, bushings, coupling including clamping and supporting as per specifications, jointing with solvent joint, testing etc. complete as directed. Note : 1.0 Only Moulded fittings shall be used for all size pipe dia , No fabricated fitting allowed . 2.0 Rigid fabricated support MS hot dip galvanized/ painted with 2 coats of synthetic enamel paint over one coat of zinc chromate primer to be provided as per dwg. for pipe sizes 200mm & above. 2.For all shaft every floor shaft signages mention with direction of flow indication. 3.For all basement level every 20mtr and at terrace level every 10mtr flow direction of pipe with type of pipes to be mentioned by vendor as per direction of site incharge. (For Terrace , building and basement Suspended lines) | 1
Galvanised rubber sleeved clamps/ u bolts, brackets (External Pipe to be fixed with zinc coated clamp, Brackets and U Bolts etc ), passivated fasteners & direction arrows and legend boards of appropriate size and spacing as directed by E-I-C shall be included in the price
Cutting and chasing in wall and floors with diamond cutter for UPVC pipes and fittings and making good the same by using 1:1 cement mortar over the mesh.
| 25 mm |  | Item
| 32 mm |  | Item
| 40 mm |  | Item
| 50 mm |  | Item
| 75 mm |  | Item
| 90 mm |  | Item
| 110 mm |  | Item
| 160 mm |  | Item
| 200 mm |  | Item
| 250mm |  | Item
| 300mm |  | Item
| c/f | [6 empty] | 0
| b/f | [6 empty] | 0
A | Providing, fixing, jointing and testing UPVC traps of self cleansing design with water seal not less than 50 mm., with or without vent, jointing with appropriate lubricant, cutting chases / hole in floors / slabs and bringing the same in proper condition and shape after placing the trap in right position in case of suspended / open plumbing. Setting the trap in 1:2:4 CC in case of concealed plumbing , etc. complete, as required. Temporary airtight PVC cover to be provided to prevent dirt entry. | 1
| 110x75x50 (Multi Floor Trap) |  | Item
| 110mm floor trap |  | Item
| 110 X 110 mm "P" TYPE - P TRAP |  | No. | 24
B | Supplying, fixing, testing and commissioning UPVC multi inlet connection / Height riser / Hopper (3 or 4 nos. of 50mm / 75mm dia pipe inlet) made of 110mm dia pipe to be fixed with inlet of "P" trap or Floor trap. Excess connections to be plugged with solid endcap. Inlet to be protected of dust entry with endcap. | 1 | No. | 24
C | Providing and fixing UPVC trap complete with C.I. grating brick masonry chamber Size 300mm x 300mm (Inside clear dimension) with water tight C.I. cover with frame of 300 x 300 mm size (inside) the weight of cover not to be less than 4.50 kg and frame not to be less than 2.70 kg as per standard design: With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 (Chamber depth maximum up to 1000mm including Excavation, backfilling, 100mm thick PCC for chamber, 230mm wall thickness with inside and outside plaster) 150 X 100 mm "P" TYPE - GULLY TRAP - 100 mm OUTLET | 1 | No. | 5
D | Providing and fixing UPVC clean out plug with suitable End cap, male threaded joint/reducer with to Pipe/fittings . complete in all respect. | 1
| 75 mm dia. |  | Item
| 110 mm dia. |  | Item
| 160 mm dia |  | Item
| 200 mm dia |  | Item
E | Providing and fixing UPVC Floor clean out plug with suitable End cap, male threaded joint/reducer with to Pipe/fittings . complete in all respect. | 1
| 75 mm dia. |  | Item
| 110 mm dia. |  | Item
| 160 mm dia |  | Item
| 200 mm dia |  | Item
C/F
B/F
A | Supply , installation , testing and commissioning of FRP top slots drainage channel Cover (Grating) with / Without frame Suitable for the specified Load class with All related item with respect to top slot drain are included in given running meter and as per standard drawing and installation direction of site incharge . Installation height will be varies as per Gradient slope at existing site. | 1
| 150mm Wide drain channel - C 250 - Truck / Temp Load |  | Item
| 200mm Wide drain channel - C 250 - Truck / Temp Load |  | m | 6
| 600mm Wide drain channel - (D 400) Trailor / Fire engine Load |  | m | 8
B | Earth Work in Excavation of required width for storm water, sewerage, water supply pipes at bottom depth up to 1.5 m including getting out the excavated soil and Refilling the soil as required in layer disposing of surplus excavated soil as directed within a lead of 50 m for all kinds of soil. | 1
| Pipes, exceeding 80 mm dia but not exceeding 300 mm dia. |  | m
C | Earth Work in Excavation of required width for storm water, sewerage, water supply pipes at bottom depth 1.5 m to 3m including getting out the excavated soil and Refilling the soil as required in layer disposing of surplus excavated soil as directed within a lead of 50 m for all kinds of soil. | 1
D | Pipes, exceeding 80 mm dia but not exceeding 300 mm dia. |  | Item
E | Providing and laying cement concrete 1:4:8 mix ( 1 coarse cement : 4 coarse Sand : 8 graded stone aggregate) for bed concrete or / and encasing including required shuttering, curing etc. complete as directed for all heights and depths. | 1
F | Constructing brick masonry manhole with bricks of class designation 75 in cement mortar 1:5 (1 cement : 5 coarse sand) with RCC top slab of 1:2:4 mix (1 coarse cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size), 150 mm thick foundation concrete 1:4:8 mix (1 coarse cement : 4 coarse sand : 8 graded stone aggregate 40 mm nominal size), inside and outside plastering 12mm thick in cement mortar 1:3 (1 coarse cement : 3 coarse sand) finished with a floating coat of neat cement inside and rough plaster on outside and making channel in cement concrete 1:2:4 mix, (1 coarse cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) neatly finished complete M.S plastic coated foot rests, complete as per standard design and approved drawings, including the cost of excavation, back filling, disposal of surplus earth, foot rests and other associated civil works including centering shuttering all complete. (Wihout manhole cover, Cover shall be paid separately in relevant items) | 1
| Type 1 - 600 x 600 x up to 600 mm deep. |  | No. | 11
| Type 2 - 900 x 800 x up to 900 mm deep. |  | Item
c/f
b/f
A | Construction of Catch Basin ( Road gully chamber ) of the following sizes in brick work in cement mortar 1:5 necessary 150mm thickness foundation concrete (1:4:8), 150mm wall thickness inside plastering 15 mm thick with cement mortar 1:4 and rough plaster 20 mm thick on outside with a floating of neat cement. Including necessary excavation in all soil types, dewatering, refilling, watering, ramming, removing the surplus excavated material up to a lead of 100 m and making good the same complete as required. The required depth of catch basin varies from 450 to 900mm . The rate includes connections to trenches / pipes. Manhole Cover shall be paid separately in relevant items) | 1
| 450 x 450 mm clear inside dimensions ( Depth Min. 450mm to Max.750mm ) |  | Item
B | Supply , Installation , testing and commissioning of FRP (Fiberglass Reinforced Polymer) Water gully chamber grating with frame design as per as per BSEN 124, IS 1726 25 ton Load in removable sections with matching frames of MS angles or making a similar size of offset in floor trimix / concrete, over open channel / chamber as per the drawings and designs and approved by architect and testing of joints complete as per direction of Engineer in Charge. Note : Min. 30% opening required in cover for entry surface water. | 1
| 450mm x 450mm |  | Item
C | Providing and fixing FRP (Fiber Reinforced Plastic) manhole cover with water tight double seal FRP Heavy duty cover with frame of load class as per IS:1726 & BS EN :124), with lock and key arrangement, for fixing on all R.C.C. Tank, fixed as per required level with appropriate cement mortar etc. complete in all respected as directed. | 1
| 600mm dia. - B125 for 4 wheeler load |  | Item
| 600mm dia. - C250 for truck / tempo load |  | Item
| 600mm X 600mm - B125 for 4 wheeler load |  | Item
| 600mm X 600mm - C250 for truck / tempo load |  | No. | 11
D | Providing & fixing manhole foot rests; poly propylene, steel reinforcement The polypropylene shall confirm to ASTM D-410 and shall be injection moulded around 12mm dia Fe-415 Steel reinforcing bar. The foot rest shall be provided in RCC walls / brick walls as per requirement of design / project manager. | 1 | Item
E | Providing and fixing rain water "KHURRAS" size 300 x 300 mm required depth with lead flashing around rainwater pipe with one piece lead sheet of 3 mm thick set on a layer of cold bitumen. Including heavy duty CI grating complete as required. | 1 | Item
F | Providing, fixing Air Admittance Valve (AAV) which is a one way valve designed to allow air to enter the plumbing drainage system when negative pressures develop in the piping system. The device shall close by gravity and seal the vent terminal at zero differential pressure (no flow conditions) and under positive internal pressures. | 1
| 110mm dia |  | Item
| 160mm dia |  | No.
C/F
B/F
| Charges for SEWER Line Connection / STORM WATER Line Connection with Municipality Network Chamber without Material (Required all necessary material and accessories will be paid in Relevant items in BOQ.) Including Liaising work with Statutory Authorities for obtaining approval. Including Labour charges for Excavation, breaking and resurfacing of PCC, RRC, Road (Bitumen / RCC) , Dewatering, Making Hole in Existing Chamber ( Maximum up to 5 Meters for any depth) must be scope of Contractors. In case of above 5 metres, Extra charges shale be payable in relevant items prior to consent has to be obtained from client / PMC / E-I-C. Contactor has to check feasibility before execution. (All official fees/ deposits will be paid by Client, Contractor shall be reimbursed After submission of original receipt) | 1
A | SEWER Line Connection with Municipality Network Chamber |  | Item
B | STORM WATER Line Connection with Municipality Network Chamber |  | Item
TOTAL OF SECTION-C INTERNAL SAVAGE/DRAINAGE NETWORK CARRIED OVER TO SUMMARY
PUMP ROOM :
A | Supplying, Installation, testing and Commissioning of Monoblock Pumps for Filter feed ((1W+1S) 100 LMP at 50m Head (Each Pump) | 1 | No. | 1
B | Supplying, Installation, testing and Commissioning of HPN system with VFD Base Submersible pumps with all necessary accessories. | 1 | No. | 1
Flow Capacity: 6 m3/hr (100LPM) each pump Head - 50 Mtrs. Pressure Tank - By Vender 1 Set = (1 Working + 1 Standby - cascade operation)
C | Supplying, Installation, testing and Commissioning of Submersible drainage sump pumps with free standing or on an auto coupling system, pump with grinder mechanism or semi open impeller for min. 40-45mm free passage. pump with temperature sensor in case of overheating, with 10mtr. cable. (1 working+ 1 standby) with Sump pit lifting assembly suitable for 2 Nos. Submersible drainage pumps in a sump of overall depth not more than 1.6 m, ready made electro – galvanized MS lifting chain , class C GI pipe header complete with discharge manifold, flanges, tee, elbow etc. complete including electrical panel, Float switch GI pipe up to the top of sump and including GI union. The installation shall be complete with all necessary indigenous accessories as required to complete the installation. | 1
| Sump Pump System FLOW:- 15 m3/hr. (250 LPM) each pump Head:- 20 Mtr. (1 Working+1 Standby - cascade operation ) Partial- 50mm Partial handling Capacity Motor:- _____kw/ _______ hp / 3Phase |  | No. | 1
D | Supply, installation, testing, commissioning Gun metal screwed end ‘Y’ type strainer with stainless steel fine mesh perforated sheet basket with necessary Nipple, Brass insert CPVC/ UPVC MTA or FTA, flange/union, nuts, bolts and washers complete as required | 1
| 40 mm Dia |  | Item
| 50 mm Dia |  | Item
E | Supply, installation, testing, commissioning Cast Iron Flange end ‘Y’ type strainer with stainless steel fine mesh perforated sheet basket with necessary flange/union, gasket, nuts, bolts and washers complete as required | 1
| 65 mm Dia |  | No. | 2
| 80 mm Dia |  | Item
| 100 mm Dia |  | Item
| 150 mm Dia |  | Item
F | Supply, Installing, testing and commissioning C.I butterfly valve (Lever operated), wafer end type class PN 16 as per I.S:13095 or BS:5155, including providing of necessary flanges, nuts & bolts (GI), gaskets etc., complete (including cost of flanges) as per drawings, specification and as directed by the Engineer's Representative. | 1
| 50 mm dia |  | Item
| 65 mm dia |  | No. | 2
| 80 mm dia |  | Item
| 100 mm dia |  | Item
| 150 mm dia |  | Item
C/F
B/F
A | Providing and fixing CI Dual plate wafer type non return valve / check valve [PN 16] With SS-304 Discs and Nitrile Rubber Lining with Bronze Disc, Seat Test Pressure 16 Kg/cm2g tested to 24 Kg/Sq.cm pressure complete with all fitting and accessories i.e. rubber gasket, flanges, union, nuts, bolts, washer etc. | 1
| 50 mm dia |  | Item |  |  |  | 2119 | 2119
| 65 mm dia |  | Item |  |  |  | 2587 | 2587
| 80 mm dia |  | Item |  |  |  | 3055 | 3055
| 100 mm dia |  | Item |  |  |  | 3679 | 3679
| 150 mm dia |  | Item |  |  |  | 5239 | 5239
| TOTAL OF SECTION-D PUMPROOM CARRIED OVER TO SUMMARY | [6 empty] | 16679
MISCELLANEOUS :
| WATER TANK COVER Providing and fixing FRP covers for Water Tanks with bleow mentioned Size and load bearing capacity water tank cover fixed with cement mortar as required. | 1
A | 600 mm dia 12.5T (For UGWT Tank) |  | No. | 6
| Providing and fixing 600 mm to 1000 mm long (As per wall thickness ) hot dipped G.I. heavy-duty Puddle flanges with epoxy coated, for water tanks as per I.S. 1239 (Class B) with Puddle Plate up to 150mm dia pipe and 'C' class heavy duty MS pipe conforming to IS 3589/IS 1239 of above 150mm to 400mm dia suitable size and welded all around the pipe fixed in walls, beams and top slab of R.C.C tanks (underground and OH Tank ) , GRP/SMC Panel tank, complete with all details in all respects and as per drawing. (Pipe puddle flange/plate size as per technical spec/sleeve details ) | 1
B | 40 mm dia (6 mm Thick plate) - GI Pipe |  | Item
C | 50 mm dia (6 mm Thick plate) - GI Pipe |  | Item
D | 65 mm dia (8 mm Thick plate) - GI Pipe |  | Item
E | 80 mm dia (8 mm Thick plate) - GI Pipe |  | Item
F | 100 mm dia (12 mm Thick plate) - GI Pipe |  | Item
G | 150 mm dia (12 mm Thick plate) - GI Pipe |  | Item
H | 200 mm dia (12 mm Thick plate) - GI Pipe |  | Item
J | 250 mm dia (12 mm Thick plate) - GI Pipe |  | Item
K | 300 mm dia (12 mm Thick plate) - GI Pipe |  | Item
| M.S. STRUCTURAL WORK | 1
L | Providing and fixing M.S. structural work fabricated from standard sections, (MS rounds, angles, channels etc.) including cutting to size, drilling, welding, including cost of fasteners in RCC structural members as directed, including two coats of synthetic paint over one coat of Zinc coated primer after surface preparation. (Note - Structural Qty. is Approx, Final Qty. as per site condition and GFC dwg.) |  | Kgs. | 300
| Providing, installation and testing of 3 layer HDPE tank with necessary connections for inlet, outlet, overflow and drain. Rate must be quoted considering lifting at all heights. Flange connections including necessary HDPE pipe, Flange to be welded by extrusion welding method with necessary stiffeners to be provided for connections above 2" dia. | 1
M | 5000 ltrs |  | No. | 1
C/F
B/F
A | Making core drills in rcc slab/walls/beam of various thickness including necessary chipping by breaker or manually to make surface rough for grouting purpose and making good the same with GP-II grouting. (Waterproofing shall not be a part of this item.) | 1
| 77 mm x up to 150 mm thick |  | Item
| 77 mm x up to 200 mm thick |  | Item
| 77 mm x up to 250 mm thick |  | Item
| 102 mm x up to 150 mm thick |  | Item
| 102 mm x up to 200 mm thick |  | Item
| 102 mm x up to 250 mm thick |  | Item
| 125 mm x up to 150 mm thick |  | Item
| 125 mm x up to 200 mm thick |  | Item
| 125 mm x up to 250 mm thick |  | Item
| 152 mm x up to 150 mm thick |  | Item
| 152 mm x up to 200 mm thick |  | Item
| 152 mm x up to 250 mm thick |  | Item
| 200 mm x up to 150 mm thick |  | Item
| 200 mm x up to 200 mm thick |  | Item
| 200 mm x up to 250 mm thick |  | Item
| 250 mm x up to 150 mm thick |  | Item
| 250 mm x up to 200 mm thick |  | Item
| 250 mm x up to 250 mm thick |  | Item
B | Supply, Installing, testing and commissioning of Solenoid valve with bypass line including 3 no's of brass ball valve and control panel, including providing of Brass Adapters, flanges/unions, nuts, bolts and washers complete including electrical work as required for applications. | 1
| 40 mm dia |  | Item
| 50 mm dia |  | Item
| 80 mm dia |  | Item
C | Providing and fixing Electronic type level indicator for water tanks mounting in panel with provision of connect to BMS including wiring with the following features, level display, alarm when water level is low or high, full range from one level to four level display and manual reset for Alarm etc. with electrical wiring conduit supports from wall & ceiling probes and all other accessories complete as required. (For Water Tanks) | 1 | Item
D | Supply, installing, testing and commissioning of annunciation and indication panel with interlocking arrangement complete in accordance to specification with level controller (In Raw Water, Domestic Water , STP Treated water tank & Fire Water Tank : High / Low Level Controller) etc with control cabling from field to MCC as required. | 1 | item
E | Installing, testing and commissioning of WATER COOLER (DRINKING WATER AREA) Type – Fully Stainless Steel Cold Water Cooler Body Material – SS-304 Stainless Steel Storage Capacity – 120 ltrs Cooling Capacity – 80 ltrs / hr Power Supply- 230V/50Hz/1Ph | 1 | Item
TOTAL OF SECTION-E MISCELLANEOUS : CARRIED OVER TO SUMMARY
RAIN WATER HARVESTING SYSTEM :
A | Construction of Rain water harvesting size 2.5 m dia x 3.5m effective depth for the re-charging of storm water run off including the civil work with following specification [Construction of Chamber]. | 1
De-Silting Chamber: Providing and constructing masonry de-silting chamber 1800mm x 1500mm with required depth inside with 75 class designated brick work in cement mortar 1:6 (1cement : 6 fine sand) with C.I double seal medium duty 560mm dia manhole cover (2Nos.). top slab 1:2:4 mix (1cement : 2coarse sand : 4 graded stone aggregate 20mm nominal size) with minimum 1.5% reinforcement, foundation concrete 1:5:10 (1cement : 5 fine sand:10 grade stone aggregate 20mm nominal size including baffle wall, necessary excavation, back filling and disposal of surface earth. Complete with inlet, outlet and overflow arrangement. Foot rest @400mm c/c, grating of required size with 16mm sq. bars and frame @20mm clear spacing fixed at month of pipe as per site conditions and direction of Engineer in charge
Drilling: Drilling percolation borehole 200mm dia with reverse rotary method in all types of soil up to 50 m (approx.) depth including cost for mobilization of rig and making good the area upon completion of work. Contractor shall arrange for all necessary tools, water and consumable and laying for drilling. Providing and laying pea gravel all around the casing pipe. Providing and laying 160 mm dia slotted UPVC pipe of 6 Kg/cm2 - 35 m -40m or as per site sub-strata or set as per direction of Engineer- in charge 160 mm dia UPVC blind pipe ( Top PVC Cover ) of 6 Kg/cm2.
Rain Water Harvesting Well Filtration Chamber: Providing and constructing rain water harvesting well/filtration chamber of size 2.5 m dia x 3.5 m eff. depth inside with 75 class designated brick work in cement motor 1:6 (1cement : 6 fine sand) with 560mm dia C.I double seal medium duty manhole cover with top slab 1:2:4 mix (1cement : 2 course sand :4 graded stone aggregate 20mm nominal size) with minimum 1.5% reinforcement , foundation concrete 1:5:10 (1cement : 5 fine sand and 10 graded stone) aggregate 20mm nominal size including 300mm duty. Boulder 10-20mm, 300mm duty, gravel 5-10mm size, 300mm depth coarse sand 1.5-2.0mm including necessary excavation, back filling and disposal of surface earth complete with inlet, outlet, overflow arrangement pvc coated Foot Rest, 100mm dia deep holes @500mm c/c to be provided 1200 c/c above the bottom of wall, 100mm C.I vent pipe -2m height with cowls. Rate shall include excavation, back filling and all other operations necessary for completing the job.
| Rain Water harvesting system complete set as per above details |  | No. | 1
RAIN WATER HARVESTING
Carried to Summary
SEWAGE TREATMENT PLANT (STP) — 6 KLD :
| Package Sewage Treatment Plant — 6 KLD capacity, Extended Aeration/MBBR technology, FRP/MS construction complete with equalization tank, aeration chamber, clarifier, tertiary filtration unit, duty+standby air blowers, diffuser grid, sludge holding zone — supply, install, test & commission |  | No. | 1
| Civil foundation, RCC platform/plinth and support structure for STP package unit |  | Item | 1
| Raw sewage collection sump (pre-treatment, screen chamber) with duty+standby submersible transfer pumps |  | No. | 1
| Air blower unit (duty+standby) with fine-bubble diffuser grid — aeration system (if not integral to package) |  | No. | 1
| Sludge drying bed / sludge handling & disposal arrangement |  | No. | 1
| Treated water storage tank — 5 KL capacity, for flushing & landscape irrigation reuse |  | No. | 1
| Treated water reuse pump set (duty+standby) with pressure control — flushing/irrigation distribution |  | No. | 1
| Chlorination / disinfection dosing system — treated water final polishing |  | No. | 1
| Odour control unit — activated carbon filter at STP vent |  | No. | 1
| STP interconnecting piping — raw sewage inlet, treated water outlet, air piping (UPVC/GI as applicable) |  | Item | 1
| STP control panel — level sensors, blower/pump interlocks, alarm, BMS interface |  | No. | 1
| Testing, commissioning & water quality compliance testing (BOD/COD/TSS as per discharge norms) |  | Item | 1
TOTAL OF SECTION-G SEWAGE TREATMENT PLANT (STP) : CARRIED OVER TO SUMMARY
EFFLUENT TREATMENT PLANT (ETP) — 4 KLD :
| Package Effluent Treatment Plant — 4 KLD capacity, physico-chemical treatment (neutralization, coagulation-flocculation, clarification, multi-media & activated carbon filtration), FRP/MS construction — supply, install, test & commission |  | No. | 1
| Civil foundation, RCC platform/plinth and support structure for ETP package unit |  | Item | 1
| Chemical effluent collection sump (acid-resistant lining) with duty+standby chemical-resistant transfer pumps |  | No. | 1
| pH neutralization system — acid/alkali dosing pumps, pH sensor & control, dosing tanks |  | No. | 1
| Coagulation-flocculation dosing system — chemical dosing pumps + tanks |  | No. | 1
| Multi-media pressure filter — post-clarification polishing |  | No. | 1
| Activated carbon filter — final effluent polishing before discharge |  | No. | 1
| Sludge dewatering / filter press (chemical sludge handling & disposal) |  | No. | 1
| Treated effluent holding tank — 3 KL capacity, acid-resistant lining, pre-discharge monitoring |  | No. | 1
| ETP interconnecting piping — acid-resistant UPVC/CPVC, chemical inlet/outlet & dosing lines |  | Item | 1
| ETP control panel — dosing pump interlocks, pH/level sensors, alarm, BMS interface |  | No. | 1
| Testing, commissioning & effluent quality compliance testing (pH/heavy metals/COD as per discharge norms) |  | Item | 1
TOTAL OF SECTION-H EFFLUENT TREATMENT PLANT (ETP) : CARRIED OVER TO SUMMARY
SUMMARY
SANITARY FIXTURES & CP FITTINGS
WATER SUPPLY (INTERNAL & EXTERNAL)
INTERNAL & EXTERNAL SEWAGE/DRAINAGE NETWORK
PUMP ROOM
MISCELLANEOUS
RAIN WATER HARVESTING
SEWAGE TREATMENT PLANT (STP)
EFFLUENT TREATMENT PLANT (ETP)
TOTAL OF All Section of Plumbing Work : CARRIED OVER TO SUMMARY

## FIRE Work_BOQ
GOLDBOD NATIONAL ASSAY CENTER · FIRE FIGHTING SYSTEM BOQ · TENTATIVE — SUBJECT TO HYDRAULIC CALC
FIRE FIGHTING SYSTEM — SPRINKLER, HYDRANT, PUMP ROOM & EXTINGUISHERS
ITEM | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
SECTION 1 — SPRINKLER SYSTEM [NFPA 13 — Ordinary Hazard labs / Light Hazard offices, from ceiling fire layout]
A | Pendent/Upright Fire Sprinkler Head — GF (64 nos: labs Ordinary Hazard + offices Light Hazard) | 64 | No
B | Pendent Fire Sprinkler Head — FF (27 nos, Light Hazard office) | 27 | No
C | Upright Fire Sprinkler Head — SF Future Expansion (52 nos, base building provision) | 52 | No
D | MS 'Patti' clamp + threaded rod hanger — sprinkler pipe support (per detail, max 3.0-3.5m spacing) | 186 | No
E | Flexible sprinkler drop connection (FS whip) — false ceiling to sprinkler head | 143 | No
SUBTOTAL — SPRINKLER HEADS & SUPPORTS
SECTION 2 — SPRINKLER PIPING — MS/GI (Colour-coded per Fire Legend Sheet)
F | 25mm dia (25Ø) MS sprinkler branch/armover pipe — Sch 40, screwed/grooved joints | 229 | m
G | 32mm dia (32Ø) MS sprinkler range pipe | 157 | m
H | 40mm dia (40Ø) MS sprinkler distribution pipe | 208 | m
J | 50mm dia (50Ø) MS sprinkler sub-main pipe | 156 | m
K | 65mm dia (65Ø) MS sprinkler main branch pipe | 114 | m
L | 80mm dia (80Ø) MS sprinkler main riser pipe | 110 | m
M | 150mm dia (150Ø) MS sprinkler main header/riser pipe (thick blue on plan) | 65 | m
N | MS pipe fittings — elbows, tees, reducers, unions (provisional 15% of pipe cost) | 1 | Item
P | Anti-corrosive painting — 2 coats red oxide + 2 coats fire-red enamel, all exposed MS pipe | 974 | m
SUBTOTAL — SPRINKLER PIPING
SECTION 3 — SPRINKLER ALARM VALVE SET & CONTROL VALVES [Per ICV / Alarm Valve Detail Sheet]
A | Sprinkler Alarm Valve (wet type) 150mm — complete with trim set: pressure gauge ×2, retard chamber, sight glass | 1 | No
B | Flow switch (FS) — sprinkler alarm valve trim, water motor gong | 1 | No
C | ICV (Isolation Control Valve) 150mm — butterfly type with tamper switch | 2 | No
D | Non-Return Valve (NRV) 150mm — sprinkler alarm valve upstream | 2 | No
E | Butterfly valve (isolation) — various sizes 65mm-150mm, per riser/zone isolation | 8 | No
F | Pressure gauge (PG) — sprinkler system monitoring points | 6 | No
G | Pressure switch (PS) — sprinkler zone monitoring, fire panel interface | 4 | No
H | Air release valve — sprinkler system high points | 4 | No
J | Strainer (bucket type) — sprinkler pump suction/alarm valve | 2 | No
K | Sprinkler drain pipe (50mm dia) + drain valve — alarm valve test/drain, per typical drain detail | 25 | m
SUBTOTAL — SPRINKLER CONTROL & ALARM VALVES
SECTION 4 — HYDRANT SYSTEM [Internal Landing Valves + External Yard Hydrants]
A | Internal Fire Hydrant Landing Valve (single-headed, 63mm outlet) — staircase landings, all floors (6 nos) | 6 | No
B | Fire Hose Cabinet (FHC) complete — landing valve + hose reel + canvas hose + branch pipe/nozzle (6 nos) | 6 | No
C | Fire Hose — canvas type, 63mm dia × 15m length, with coupling | 12 | No
D | Hose Reel with nozzle — 25mm dia × 30m, swing type | 6 | No
E | External Fire Hydrant (double-headed, stand post type, 63mm×2 outlets) — site perimeter (6 nos) | 6 | No
F | 150mm dia (150Ø) MS/DI hydrant ring main pipe — internal + external perimeter loop (thick red on plan) | 155 | m
G | Fire Brigade Breeching Inlet (4-way, 63mm) — external, near main entry, per typical detail | 2 | No
H | MS pipe fittings — hydrant system elbows, tees, reducers (provisional 12%) | 1 | LS
J | Anti-corrosive painting — 2 coats red oxide + fire-red enamel, hydrant pipe | 155 | m
SUBTOTAL — HYDRANT SYSTEM
SECTION 5 — FIRE PUMP ROOM [UG Tank + Pump Room — Per Presentation Layout]
A | Underground Fire Water Storage Tank — RCC, min 150 KL capacity (per NFPA sprinkler+hydrant demand, TBC by hydraulic calc) | 1 | No
B | Electric Fire Pump (Main) — centrifugal, min 1520 LPM @ 7 bar (capacity TBC by hydraulic calc) | 1 | No
C | Diesel Engine Fire Pump (Standby) — matching duty to electric pump, with exhaust piping | 1 | No
D | Electric Jockey Pump — pressure maintenance, min 180 LPM @ 7.5 bar | 1 | No
E | Fire Pump Control Panel — auto/manual, with pressure switches, alarm annunciation, battery backup | 1 | No
F | Diesel pump exhaust piping + silencer + smoke outlet louvre (per detail: 'Detail of Fire Diesel Exhaust Pipe') | 1 | No
G | Pump room suction + delivery header piping, valves, pressure gauges, NRVs — complete pump set interconnection | 1 | No.
H | Diesel storage tank (day tank) for standby pump — min 250L capacity with fuel level gauge | 1 | No
SUBTOTAL — FIRE PUMP ROOM
SECTION 6 — PORTABLE FIRE EXTINGUISHERS [Per Fire Legend Symbol Schedule]
J | ABC Type Dry Powder Fire Extinguisher — 6kg, wall-mounted (1 per ~200m², 13 nos) | 13 | No
K | CO2 Type Fire Extinguisher — 4.5kg, electrical/server rooms (6 nos) | 6 | No
L | Fire Extinguisher Trolley Type (K11.5, 50kg) — General Melting/high-hazard zone (1 no) | 1 | No
M | Extinguisher wall bracket/stand + signage — all locations | 20 | No
SUBTOTAL — PORTABLE EXTINGUISHERS
SECTION 7 — TESTING, COMMISSIONING & CERTIFICATION
A | Hydrostatic pressure testing — complete sprinkler + hydrant piping network | 1 | Item
B | Fire pump performance test — flow/pressure test at rated duty point, with certified report | 1 | Item
C | Fire alarm/sprinkler flow switch interface test — integration with fire alarm panel | 1 | Item
D | As-built drawings, O&M manuals, NFPA compliance certification, handover documentation | 1 | Item
SUBTOTAL — TESTING & COMMISSIONING
SUMMARY
SPRINKLER HEADS & SUPPORTS
SPRINKLER PIPING
SPRINKLER CONTROL & ALARM VALVES
HYDRANT SYSTEM
FIRE PUMP ROOM
PORTABLE EXTINGUISHERS
TESTING & COMMISSIONING
FIRE FIGHTING SYSTEM
TOTAL CARRIED TO SUMMARY

## Loose Furniture
FURNITURE SUPPLY
ITEM | LOCATION | DESCRIPTION | QTY | UNIT | RATE | AMOUNT
── GF ──
A | GF – Reception | Reception Desk | 1 | No
B | GF – Reception | Receptionist Chair | 2 | No
C | GF – Reception | 3-Seater Sofa (dark grey leather) | 2 | No
D | GF – Reception | Single Lounge Chair | 4 | No
E | GF – Reception | Coffee Table (marble top) | 2 | No
F | GF – Reception | Side Table | 2 | No
G | GF – Reception | Decorative Gold Sculpture | 1 | No
H | GF – Reception | Pendant Light Cluster | 1 | No
J | GF – Reception | Indoor Planter / Tree | 4 | No
K | GF – Reception | Artwork Panel (framed) | 5 | No
L | GF – Waiting | 2-Seater Sofa | 4 | No
M | GF – Waiting | Single Armchair | 6 | No
N | GF – Waiting | Coffee Table | 4 | No
P | GF – Waiting | Side Table | 3 | No
Q | GF – Obs Room | Observation Counter Bench (3600mm) | 4 | No
R | GF – Obs Room | Mesh Chair (ergonomic) | 8 | No
S | GF – Obs Room | Lounge Chair | 4 | No
T | GF – Sample Prep Lab | Lab Work Bench (2400mm) | 6 | No
U | GF – Sample Prep Lab | Under-bench Cabinet (lockable) | 12 | No
V | GF – Sample Prep Lab | Lab Stool (height-adj) | 10 | No
W | GF – Sample Prep Lab | Overhead Wall Shelf Unit | 4 | No
X | GF – Lab XRF+Wt | Lab Bench (XRF, 1800mm) | 5 | No
Y | GF – Lab XRF+Wt | Under-bench Cabinet | 10 | No
Z | GF – Lab XRF+Wt | Lab Stool | 10 | No
AA | GF – Lab XRF+Wt | Instrument Trolley (mobile) | 6 | No
AB | GF – Lab Admin | Office Desk 1600mm | 4 | No
C/F
B/F
A | GF – Lab Admin | Ergonomic Office Chair | 6 | No
B | GF – Lab Admin | Filing Cabinet 2-door | 6 | No
C | GF – Lab Admin | Visitor Chair | 6 | No
D | GF – Vault Ante | Security Desk | 2 | No
E | GF – Vault Ante | Security Chair | 46 | No
F | GF – CCTV Room | CCTV Monitoring Desk (corner) | 4 | No
G | GF – CCTV Room | Operator Chair | 8 | No
H | GF – CCTV Room | Server Rack Cabinet (19" 18U) | 6 | No
J | GF – Staff Lock | Steel Locker Unit (6-door) | 15 | No
K | GF – Staff Lock | Changing Bench (timber 1800mm) | 6 | No
L | GF – Pantry | Pantry Counter with Sink | 6 | No
M | GF – Pantry | Bar Stool | 6 | No
N | GF – Security Rm | Security Desk | 4 | No
P | GF – Security Rm | Operator Chair | 6 | No
Q | GF – Security Rm | Visitor Chair | 8 | No
R | GF – Fire Assay | Lab Bench acid-resistant 2400mm | 10 | No
S | GF – Fire Assay | Under-bench Cabinet | 15 | No
T | GF – Fire Assay | Lab Stool | 15 | No
U | GF – Melting | Mobile Equipment Trolley | 8 | No
V | GF – Melting | Safety Signage Board | 15 | No
Carried Forward
Brought Forward
── FF ──
A | FF – CEO (5.95×6m) | Executive Desk (marble top, 2400mm) | 2 | No
B | FF – CEO (5.95×6m) | High-back Executive Chair (leather) | 2 | No
C | FF – CEO (5.95×6m) | Visitor Armchair | 6 | No
D | FF – CEO (5.95×6m) | Side Credenza (wood veneer 1800mm) | 4 | No
E | FF – CEO (5.95×6m) | Round Coffee Table | 4 | No
F | FF – CEO (5.95×6m) | Floor Lamp (designer) | 10 | No
G | FF – CEO (5.95×6m) | Artwork Panel (large) | 4 | No
H | FF – CEO (5.95×6m) | Area Rug (2000×3000mm) | 4 | No
J | FF – Dir (5.95×4m) | Executive Desk 1800mm | 4 | No
K | FF – Dir (5.95×4m) | High-back Executive Chair | 4 | No
L | FF – Dir (5.95×4m) | Visitor Chair | 8 | No
M | FF – Dir (5.95×4m) | Bookshelf with LED | 4 | No
N | FF – Cabin-01 | Office Desk 1400mm | 3 | No
P | FF – Cabin-01 | Ergonomic Chair | 4 | No
Q | FF – Cabin-01 | Visitor Chair | 4 | No
R | FF – Cabin-02 (3.87×5m) | Office Desk 1400mm | 4 | No
S | FF – Cabin-02 (3.87×5m) | Ergonomic Chair | 4 | No
T | FF – Cabin-02 (3.87×5m) | Visitor Chair | 4 | No
U | FF – Cabin-02 (3.87×5m) | Pedestal Cabinet | 4 | No
V | FF – Workspace (14.83×9.45m) | Office Work Desk (1400×700mm bench) | 40 | No
W | FF – Workspace (14.83×9.45m) | Ergonomic Mesh Chair | 40 | No
Carried Forward
Brought Forward
A | FF – Workspace (14.83×9.45m) | Under-desk Pedestal (3-drawer) | 40 | No
B | FF – Workspace (14.83×9.45m) | Overhead Storage Locker | 20 | No
C | FF – Workspace (14.83×9.45m) | Acoustic Panel Partition (row divider) | 12 | No
D | FF – Conf (8.90×5.75m) | Boardroom Table (30-seat, stone inlay) — v4 | 6 | No
E | FF – Conf (8.90×5.75m) | Conference Chair (leather, gold base) | 36 | No
F | FF – Conf (8.90×5.75m) | Credenza (AV+storage, 3600mm) | 4 | No
G | FF – Conf (8.90×5.75m) | Projection Screen (motorised, 3000mm) | 4 | No
H | FF – Dining (10.17×9.45m) | Dining Table (4-seater, 1200×600mm) | 10 | No
J | FF – Dining (10.17×9.45m) | Dining Chair (stackable) | 36 | No
K | FF – Dining (10.17×9.45m) | Serving Counter / Buffet Unit | 4 | No
L | FF – Dining (10.17×9.45m) | Display Shelf (plants/décor) | 6 | No
M | FF – Dining (10.17×9.45m) | Display Shelf (plants/décor) | 6 | No
── SF ──
N | SF – Lobby | Seating Bench (near lift) | 6 | No
P | SF – Lobby | Indoor Plant (potted) | 20 | No
TOTAL CARRIED TO SUMMARY — FURNITURE

## Security Frisking _BOQ
GOLDBOD NATIONAL ASSAY CENTER · SECURITY SYSTEMS BOQ ·
SECTION 01 — VEHICLE ACCESS CONTROL — MAIN VISITORS GATE
ITEM | DESCRIPTION | MIN. SPECIFICATION / STANDARD REF | QTY | UNIT | RATE | AMOUNT
SEC-01 — CRASH-RATED SLIDING GATE — Main Visitors Gate / Perimeter Vehicle Entry
A | RAKSHAK 4 (K4 Crash-Rated Sliding Gate) — complete supply, install, T&C K4 / IWA 14-1:2013, PAS 68, ASTM F2656 or equivalent — 7.2t N2A class @ ~48km/h, low/zero penetration High-grade structural steel gate leaf, heavy-duty bottom guide/rail, guide posts, anti-lift/anti-tamper Motorized with manual override; photo sensors, loop detectors, warning light, emergency stop Hot-dip galvanized + epoxy/PU RAL coating; integrated with ACS, CCTV, IDS, guard intercom | K4 / IWA 14-1:2013, PAS 68, ASTM F2656 or equivalent — 7.2t N2A class @ ~48km/h, low/zero penetration High-grade structural steel gate leaf, heavy-duty bottom guide/rail, guide posts, anti-lift/anti-tamper Motorized with manual override; photo sensors, loop detectors, warning light, emergency stop Hot-dip galvanized + epoxy/PU RAL coating; integrated with ACS, CCTV, IDS, guard intercom | 1 | No
SEC-02 — CRASH-RATED TYRE KILLER — Main Gate Approach Lane
B | Active 2-way spike tyre killer (D100H hydraulic / D100M electro-mechanical or equivalent) Crash-tested; hardened high-tensile carbon steel spikes, rated height ~150mm Galvanized MS body, powder-coated, internal drainage Push button / remote / ACS / guard control; manual operation on power failure Vehicle loop detector, photo sensor, warning signage/traffic lights; IP68 rated | Crash-tested; hardened high-tensile carbon steel spikes, rated height ~150mm Galvanized MS body, powder-coated, internal drainage Push button / remote / ACS / guard control; manual operation on power failure Vehicle loop detector, photo sensor, warning signage/traffic lights; IP68 rated | 1 | No
c/f
b/f
SEC-03 — CRASH-RATED BOLLARDS — Main Gate & Vehicle Stand-off Points
A | Hydraulic/pneumatic retractable crash-rated bollards (S4-H/S4-P or equivalent)IWA 14-1 / PAS 68 / ASTM F2656 — 7.2t vehicle @ ~48-50km/h Ø~223mm high-tensile carbon steel cylinder, SS304/316 sleeve or RAL finish PLC-based control, group + individual maintenance mode, manual override Loop detector, photo sensor, red LED/reflective bands Dedicated foundation, drainage sump/pipe, conduits, HPU/control cabinet incl. in rate | IWA 14-1 / PAS 68 / ASTM F2656 — 7.2t vehicle @ ~48-50km/h Ø~223mm high-tensile carbon steel cylinder, SS304/316 sleeve or RAL finish PLC-based control, group + individual maintenance mode, manual override Loop detector, photo sensor, red LED/reflective bands Dedicated foundation, drainage sump/pipe, conduits, HPU/control cabinet incl. in rate | 6 | No
SEC-04 — BOOM BARRIER — Vehicle Approach / Preliminary Control
B | Heavy-duty electro-mechanical boom barrier (PAT 6D or equivalent) Boom length up to 6m telescopic; 100% duty cycle outdoor rated Opening/closing ~4-6 sec; galvanized/SS housing, IP67 Loop detector, photocell, traffic light, red/green LED boom, manual override, slow start/stop Note: Boom barrier is traffic control only — NOT counted as crash-rated protection | Boom length up to 6m telescopic; 100% duty cycle outdoor rated Opening/closing ~4-6 sec; galvanized/SS housing, IP67 Loop detector, photocell, traffic light, red/green LED boom, manual override, slow start/stop Note: Boom barrier is traffic control only — NOT counted as crash-rated protection | 2 | No
C/F
B/F
SEC-05 — INTERLOCKED CRASH-RATED ROLLING SHUTTERS — Bullion Van Vehicle Airlock
A | Motorized heavy-duty rolling shutter — security-rated slats, PRICED AS ONE INTEGRATED SYSTEM System: 2 nos electronically interlocked shutters forming vehicle sally-port/airlock Interlock logic: outer opens on authorization → vehicle enters holding bay → outer closes & confirmed → inner opens only after verification. Simultaneous opening PREVENTED in normal operation Heavy-duty galvanized steel slats, side guides, locking bars, hood, barrel, motor, limit switches Bottom safety edge, photo sensors, manual override; PLC/security controller w/ status feedback Crash/forced-entry/fire rating per Security Consultant & fire strategy Rate below is PER SHUTTER — treat as one integrated airlock system per BOQ note | System: 2 nos electronically interlocked shutters forming vehicle sally-port/airlock Interlock logic: outer opens on authorization → vehicle enters holding bay → outer closes & confirmed → inner opens only after verification. Simultaneous opening PREVENTED in normal operation Heavy-duty galvanized steel slats, side guides, locking bars, hood, barrel, motor, limit switches Bottom safety edge, photo sensors, manual override; PLC/security controller w/ status feedback Crash/forced-entry/fire rating per Security Consultant & fire strategy Rate below is PER SHUTTER — treat as one integrated airlock system per BOQ note | 2 | No
B | PLC Interlock Controller + Status Feedback Panel — vehicle airlock system Shutter open/closed/locked status, bollard up/down, emergency stop, fire alarm condition, manual override Integration with ACS, CCTV, IDS, fire/emergency strategy per approved sequence | Shutter open/closed/locked status, bollard up/down, emergency stop, fire alarm condition, manual override Integration with ACS, CCTV, IDS, fire/emergency strategy per approved sequence | 1 | LS
SEC-06 — BOMB / EXPLOSIVE DETECTION ZONE — Bullion Van Inspection Zone
C | Under-vehicle inspection/scanning system (UVSS) — fixed or portable. High-resolution imaging of vehicle underside, image capture/archive, operator display Final equipment configuration per Security Consultant confirmation | High-resolution imaging of vehicle underside, image capture/archive, operator display Final equipment configuration per Security Consultant confirmation | 1 | No
| c/f | C/F
| b/f | B/F
A | Handheld Explosive Trace Detector (ETD) Trace detection of explosive residues; calibration kit; operator training included | Trace detection of explosive residues; calibration kit; operator training included | 2 | No
B | Handheld Metal Detector — vehicle/personnel inspection. Portable, rechargeable battery, audible/vibration alarm | Portable, rechargeable battery, audible/vibration alarm | 3 | No
C | Inspection Mirrors (under-vehicle, telescopic) + Portable Search Lighting. Telescopic under-vehicle mirror with LED illumination, wheeled trolley | Telescopic under-vehicle mirror with LED illumination, wheeled trolley | 2 | No
D | High-resolution CCTV coverage — bullion inspection zone (fixed + PTZ). High-lux/low-light IP cameras with analytics; coverage per GNAC-SEC-001 Table 16 Includes guard workstation display integration | High-lux/low-light IP cameras with analytics; coverage per GNAC-SEC-001 Table 16 Includes guard workstation display integration | 4 | No
E | Inspection Bay Civil/MEPF Interface — power, UPS, data, high-lux lighting, drainage, covered inspection area. Emergency stop/panic alarm at inspection point; equipment storage/charging point | Emergency stop/panic alarm at inspection point; equipment storage/charging point | 1 | LS
C/F
B/F
SEC-07 — WALK-THROUGH METAL DETECTOR (WTMD) — Visitor Entry + Staff Screening Route
A | Multi-zone Walk-Through Metal Detector — complete supply, install, T&C Adjustable sensitivity, multi-zone visual indication, audible/visual alarm Self-diagnostics, event count/logging, tamper-resistant control panel NIJ 0601.02 or equivalent; CE/IEC electrical safety, EMC, radiation/non-ionizing safety UPS-backed supply, dedicated power point, guard monitoring position Locations: (1) Main visitor entry, (2) Staff main entry, (3) Second WTMD before lab area | Adjustable sensitivity, multi-zone visual indication, audible/visual alarm Self-diagnostics, event count/logging, tamper-resistant control panel NIJ 0601.02 or equivalent; CE/IEC electrical safety, EMC, radiation/non-ionizing safety UPS-backed supply, dedicated power point, guard monitoring position Locations: (1) Main visitor entry, (2) Staff main entry, (3) Second WTMD before lab area | 3 | No
| c/f | C/F
| b/f | B/F
SEC-08 — X-RAY BAGGAGE SCANNER — Pedestrian Entry / Luggage Screening
A | Conveyorized X-ray baggage scanner — complete supply, install, T&C. High-resolution image display, enhancement, zoom, colour/material discrimination, threat marking Lead shielding, safety curtains, key switch, warning lamps, interlocks, emergency stop Radiation leakage test certificate + Ghana radiation authority compliance Operator workstation, level floor, UPS/power supply, queueing/inspection space Includes calibration, operator training, annual service support (1st year) | High-resolution image display, enhancement, zoom, colour/material discrimination, threat marking Lead shielding, safety curtains, key switch, warning lamps, interlocks, emergency stop Radiation leakage test certificate + Ghana radiation authority compliance Operator workstation, level floor, UPS/power supply, queueing/inspection space Includes calibration, operator training, annual service support (1st year) | 1 | No
SEC-09 — ACCESS-CONTROL FLAP BARRIERS — Staff Main Entry After WTMD
B | Bi-directional flap barrier / speed gate — card/biometric access. Stainless steel body, tempered glass/acrylic flaps, concealed drive Card reader + biometric reader, controller, emergency release, event log Anti-tailgating sensors, obstruction detection, soft-closing flaps Fire alarm release/open mode, battery backup; ACS/CCTV/fire alarm integration | Stainless steel body, tempered glass/acrylic flaps, concealed drive Card reader + biometric reader, controller, emergency release, event log Anti-tailgating sensors, obstruction detection, soft-closing flaps Fire alarm release/open mode, battery backup; ACS/CCTV/fire alarm integration | 3 | No
C/F
B/F
SEC-10 — BIOMETRIC / ACCESS-CONTROL DOORS — Controlled Doors in Staff/Security Sequence
A | Biometric/card access-control door set — complete hardware + integration. Card/biometric reader, electromagnetic lock/electric strike as suitable Door position sensor, request-to-exit, emergency break-glass Access logs at security workstation; dual authentication for high-security zones Fail-safe/fail-secure mode coordinated with fire/life safety strategy Locations: Lab entry doors, vault ante-room, staff lockers, security room, sample transfer zones | Card/biometric reader, electromagnetic lock/electric strike as suitable Door position sensor, request-to-exit, emergency break-glass Access logs at security workstation; dual authentication for high-security zones Fail-safe/fail-secure mode coordinated with fire/life safety strategy Locations: Lab entry doors, vault ante-room, staff lockers, security room, sample transfer zones | 8 | No
SEC-11 — FRISKING BOOTH — Before Working / Laboratory Area Entry
B | Privacy-controlled frisking booth — complete civil + fit-out. Durable partition/wall finish, anti-slip floor, adequate lighting Guard/operator position, tray/hooks as required, clear entry/exit control CCTV covering approach/exit only (privacy protocol) — not interior Integration with WTMD/access-control sequence and guard SOP Provision: separate booths for staff screening sequence (2 nos per drawing) | Durable partition/wall finish, anti-slip floor, adequate lighting Guard/operator position, tray/hooks as required, clear entry/exit control CCTV covering approach/exit only (privacy protocol) — not interior Integration with WTMD/access-control sequence and guard SOP Provision: separate booths for staff screening sequence (2 nos per drawing) | 2 | No
C/F
B/F
SEC-12 — SECURE SLIDING HATCH — Gold / Sample Transfer Interface
B | Secure transfer hatch — public/sampling interface to controlled internal area. Powder-coated steel / stainless steel frame construction Secure sliding panel or drawer/tray, tamper-resistant lock, internal stop Smooth heavy-duty runners; interlock/controlled opening — no direct hand access to secure area CCTV coverage + access-control logging if electronically operated Finish to match surrounding security partition; edges smooth and safe to touch Locations: 3 nos per drawing — visitor/sampling interface, receiving bay, vault ante-room transfer | Powder-coated steel / stainless steel frame construction Secure sliding panel or drawer/tray, tamper-resistant lock, internal stop Smooth heavy-duty runners; interlock/controlled opening — no direct hand access to secure area CCTV coverage + access-control logging if electronically operated Finish to match surrounding security partition; edges smooth and safe to touch Locations: 3 nos per drawing — visitor/sampling interface, receiving bay, vault ante-room transfer | 3 | No
C | Interlock Controller + CCTV Integration — sliding hatch electronic control. Electronic interlock preventing simultaneous dual-side access Integration with central ACS/CCTV event logging | Electronic interlock preventing simultaneous dual-side access Integration with central ACS/CCTV event logging | 3 | No
Total Carried to Summary

## ELV WORK_BOQ
GOLDBOD NATIONAL ASSAY CENTER · SECURITY SYSTEMS BOQ · SPEC REF GNAC-SEC-001
SECTION 05 — SECURITY SYSTEM INTEGRATION — ACS / CCTV / IDS
ITEM | DESCRIPTION | MIN. SPECIFICATION / STANDARD REF | QTY | UNIT | RATE | AMOUNT
SEC-13 — SECURITY COMMAND INTEGRATION — Security Room / CCTV & Surveillance Room
A | Access Control System (ACS) — central server/controller Doors, flap barriers, readers, biometrics, visitor credentials User levels, time zones, event logging; software licences included | Doors, flap barriers, readers, biometrics, visitor credentials User levels, time zones, event logging; software licences included | 1 | Item
B | CCTV System — IP cameras with analytics, NVR, VMS software. Coverage: all gates, vehicle barriers, bullion inspection zone, pedestrian screening, access-controlled doors, sliding hatch, frisking approach, lobby, security-critical corridors Estimated 48 camera coverage points across facility (fixed + PTZ mix) NVR storage 30-day retention, VMS software licence, monitor wall | Coverage: all gates, vehicle barriers, bullion inspection zone, pedestrian screening, access-controlled doors, sliding hatch, frisking approach, lobby, security-critical corridors Estimated 48 camera coverage points across facility (fixed + PTZ mix) NVR storage 30-day retention, VMS software licence, monitor wall | 1 | Item
C | Intrusion Detection System (IDS). Door contacts, shutter status, tamper alarms, panic alarms Barrier fault alarms, after-hours perimeter events → security control room | Door contacts, shutter status, tamper alarms, panic alarms Barrier fault alarms, after-hours perimeter events → security control room | 1 | Item
c/f
b/f
A | Security Control Desk / Workstation — dual-room configuration. Live camera views, gate/shutter/bollard states, WTMD alarms ACS events, manual release/deny functions per permissions 2 nos security rooms per drawing (main GF + secondary near gate) | Live camera views, gate/shutter/bollard states, WTMD alarms ACS events, manual release/deny functions per permissions 2 nos security rooms per drawing (main GF + secondary near gate) | 2 | No
B | Network / Cabling Infrastructure — dedicated secure VLAN. Industrial cable routing, conduit/trunking, surge protection Outdoor-rated cabling, proper labelling per facility standard | Industrial cable routing, conduit/trunking, surge protection Outdoor-rated cabling, proper labelling per facility standard | 1 | Item
C | UPS & Power Backup — controllers, panels, NVR, PLC, WTMD, X-ray scanner. Dedicated UPS circuits for all security-critical equipment Vehicle barriers: manual operation/fail-safe strategy on power loss | Dedicated UPS circuits for all security-critical equipment Vehicle barriers: manual operation/fail-safe strategy on power loss | 1 | Item
D | Fire Alarm Interface — security lockdown/release logic. Emergency egress compliance; approved by fire consultant + Security Consultant Integration with building fire alarm panel | Emergency egress compliance; approved by fire consultant + Security Consultant Integration with building fire alarm panel | 1 | Item
Carried Forward
Brought Forward
INSTALLATION, TESTING & COMMISSIONING — Per GNAC-SEC-001 Section 10
A | Civil/Foundation Works Coordination — gate, bollards, tyre killer, boom barrier, shutters. Vendor tested foundation details, structural engineer approval, drainage to pits/trenches | Vendor tested foundation details, structural engineer approval, drainage to pits/trenches | 1 | Item
B | Electrical Works — isolators, control panels, earthing, surge protection, UPS circuits. Labelled conduits, accessible maintenance panels per all security equipment. Labelled conduits, accessible maintenance panels per all security equipment | Labelled conduits, accessible maintenance panels per all security equipment | 1 | Item
C | Site Acceptance Tests (SAT) — full system. Open/close cycles, safety sensor tests, obstruction tests, loop detector tests Manual override, power failure mode, ACS/CCTV/IDS interface, event log verification, emergency stop | Open/close cycles, safety sensor tests, obstruction tests, loop detector tests Manual override, power failure mode, ACS/CCTV/IDS interface, event log verification, emergency stop | 1 | Item
D | Vehicle Airlock Interlock Test — bullion gate rolling shutters. Confirm outer/inner cannot open together, fault handling, status feedback visible Emergency/fire mode matches approved sequence — certified test report | Confirm outer/inner cannot open together, fault handling, status feedback visible Emergency/fire mode matches approved sequence — certified test report | 1 | Item
C/F
B/F
A | Crash-Rating Certification Review & Submission — SEC-01, SEC-03. Verify valid crash-test certificates for sliding gate + bollards before procurement Submission to Security Consultant and PMC for appro | Verify valid crash-test certificates for sliding gate + bollards before procurement Submission to Security Consultant and PMC for approval | 1 | Item
B | X-Ray Scanner Radiation Safety Certification. Radiation leakage test, operator radiation safety certification Compliance documentation with Ghana radiation authority | Radiation leakage test, operator radiation safety certification Compliance documentation with Ghana radiation authority | 1 | Item
C | Training — security staff, facility manager, maintenance team | ca | 1 | Item
D | As-Built Documentation, O&M Manuals, Warranty Certificates & Handover. As-built wiring diagrams, O&M manuals, maintenance schedule Spare parts list, admin credentials handover, training sign-off | As-built wiring diagrams, O&M manuals, maintenance schedule Spare parts list, admin credentials handover, training sign-off | 1 | Item
TOTAL CARRIED TO SUMMARY — 06-COMMISSIONING

## Water Bodies_BOQ
PROJECT 134 · GOLDBOD NATIONAL ASSAY CENTER · BOQ — WATER BODIES — DIMENSIONS FROM DRAWINGS
SECTION WB-A — DECORATIVE WATER BODY — DOUBLE HEIGHT ENTRANCE LOBBY [SPEC INT-WB-001]
ITEM | DESCRIPTION | L(m) | W(m) | H/D(m) | QTY | UNIT | RATE | AMOUNT
1.0 CIVIL BASIN & WATERPROOFING [Overall 2.56m × 2.56m ¦ water zone 2.05m × 2.05m ¦ depth 300mm (UFL -300) ¦ central plinth 1.01m × 1.01m]
A | Surface preparation of RCC recessed basin (2.56m × 2.56m × 300mm deep) — smooth substrate, crack repair, corner fillets, sealing of service penetrations, complete. [Base 2.56×2.56 + sides 4×2.56×0.30] | 2.56 | 2.56 | 0.3 | 10 | m²
B | Flexible chemical waterproofing system suitable for permanent water retention (Sika/Mapei/Fosroc/Ardex or appr. eq.) to base, sides, central plinth & all penetrations, incl. reinforcement treatment at corners/junctions/pipe sleeves/cable entries and mandatory 72-hour water ponding test before stone installation. [Base 6.55 + sides 3.07 + plinth sides 4×1.01×0.30 + plinth top 1.01×1.01] |  |  |  | 12 | m²
C | 40mm thk. protection screed / base coat over waterproofing to basin floor | 2.56 | 2.56 | 0.04 | 7 | m²
2.0 STONE & METAL FINISHES
D | 20mm thk. bedding coat + 20mm thk. selected black granite to all internal visible surfaces — water-zone floor, basin sides, 255mm perimeter edge band & central plinth (sides + top), fixed with water-compatible stone adhesive over protected waterproofing (plain cement-sand fixing not acceptable in water zone), incl. 6×6mm / 10×10mm grooves as per details & non-staining neutral-cure sealant + water-resistant grout. [Floor (2.05²−1.01²) + sides 4×2.05×0.30 + edge band (2.56²−2.05²) + plinth 4×1.01×0.30 + 1.01²] |  |  |  | 10 | m²
E | 1.0mm thk. folded stainless steel (SS316/SS304) edge channel/trim with approved black finish at water-zone perimeter, straight, level & corrosion resistant, incl. SS components at inlet/outlet |  |  |  | 8 | R.mt
3.0 MEP — CIRCULATION, LIGHTING & TESTING
F | Closed-loop recirculation system — low-noise pump + filter set (Grundfos/Wilo/Lowara/Pentair/Oase or appr. eq.) with sump, valves & accessible service provisions, as per MEPF details |  |  |  | 1 | No.
G | Concealed uPVC/CPVC/PPR/SS pipework — inlet, outlet, drain & overflow connected to approved drainage, leak tested before closure, complete with sleeves, glands & supports, as per MEPF |  |  |  | 1 | Item
H | IP68 underwater LED profile light, warm white 3000K, 24V DC, drivers in dry accessible area, RCCB/ELCB/GFCI protected circuit (iGuzzini/LED Linear/Signify or appr. eq.), at water-zone perimeter |  |  |  | 8.2 | m
J | Testing, commissioning, water balancing & final cleaning of complete water body |  |  |  | 1 | Item
C/F
B/F
4.0 SCULPTURE [SEPARATE BOQ ITEM — SPEC INT-WB-001 §9]
A | Custom gold-finish FRP/GRP sculpture on central plinth (1.01m × 1.01m) — FRP fabrication, internal support, metallic gold PU/clear protective coat, concealed stable fixing, sample approval, installation, protection & final cleaning, as per approved design intent |  |  |  | 1 | No.
TOTAL CARRIED TO SUMMARY — WB-A DOUBLE HEIGHT LOBBY
SECTION WB-B — DECORATIVE WATER BODY — EXECUTIVE STAIRCASE / LOBBY WATER FEATURE [SPEC INT-WB-002]
ITEM | DESCRIPTION / SPECIFICATION | L(m) | W(m) | H/D(m) | QUANTITY | UNIT | RATE | AMOUNT
1.0 CIVIL BASIN & WATERPROOFING [Water body 3.42m × 8.12m ¦ depth 300mm (UFL -300) ¦ sump zone UFL -750 ¦ central plinth 1.20m × 1.20m ¦ 3 bubblers]
A | Surface preparation of RCC recessed trough (3.42m × 8.12m × 300mm deep, extending below/around executive staircase) — smooth substrate, crack repair, corner fillets, sealing of service penetrations, complete. [Base 3.42×8.12 + sides 2×(3.42+8.12)×0.30] | 3.42 | 8.12 | 0.3 | 35 | m²
B | Flexible chemical waterproofing system suitable for permanent water retention (Sika/Mapei/Fosroc/Ardex or appr. eq.) to base, sides, sump zone (UFL -750), central plinth, overflow/skimmer zone & all penetrations (bubblers, lighting cables, pipe sleeves), incl. reinforcement treatment and mandatory 72-hour water ponding test before stone installation. [Base 27.77 + sides 6.92 + sump extra walls 4×0.60×0.45 + plinth sides 4×1.20×0.30 + plinth top 1.20²] |  |  |  | 39 | m²
C | 40mm thk. protection screed / base coat over waterproofing to basin floor | 3.42 | 8.12 | 0.04 | 28 | m²
D | 20mm thk. bedding coat + 20mm thk. selected black granite to all internal visible surfaces — basin floor, sides & central plinth (sides + top), fixed with water-compatible stone adhesive over protected waterproofing (plain cement-sand fixing not acceptable in water zone), incl. 10×10mm grooves where shown & non-staining neutral-cure sealant + water-resistant grout. Surrounding staircase/lobby stone measured elsewhere as per interior finish schedule. [Floor (27.77−1.44) + sides 6.92 + plinth 4×1.20×0.30 + 1.20²] |  |  |  | 36 | m²
E | 1.0mm thk. folded stainless steel (SS316/SS304) edge channel/trim with approved black/dark finish at basin perimeter, straight, level & corrosion resistant |  |  |  | 23 | m
3.0 MEP — CIRCULATION, BUBBLERS, LIGHTING & TESTING
F | Closed-loop recirculation system — low-noise pump + filter set (Grundfos/Wilo/Lowara/Pentair/Oase or appr. eq.) in sump (UFL -750), with valves & accessible service provisions, as per MEPF details |  |  |  | 1 | No.
G | Concealed bubbler/nozzle system with controlled gentle bubbling effect — adjustable & balanced at commissioning, no splashing on adjacent staircase/flooring, no exposed pipework, complete |  |  |  | 3 | No.
H | Overflow / skimmer arrangement connected to approved drainage to prevent accidental lobby flooding, complete |  |  |  | 1 | No.
J | Concealed uPVC/CPVC/PPR/SS pipework — inlet, outlet & drain, leak tested before closure, complete with sleeves, glands & supports, as per MEPF |  |  |  | 1 | Lot
C/F
B/F
A | IP68 underwater LED profile light, warm white 3000K, 24V DC, drivers in dry accessible area, RCCB/ELCB/GFCI protected circuit (iGuzzini/LED Linear/Signify or appr. eq.), at basin perimeter |  |  |  | 23 | m
B | Testing, commissioning, bubbler flow balancing & final cleaning of complete water body |  |  |  | 1 | Item
4.0 SCULPTURE [SEPARATE BOQ ITEM — SPEC INT-WB-002 §9]
C | Custom FRP/GRP sculpture with rustic brass metallic finish (water-based gold refining / gold panning concept) on central plinth (1.20m × 1.20m) — FRP fabrication, internal support, protective clear coat, concealed stable fixing, sample approval, installation, protection & final cleaning, as per approved design intent |  |  |  | 1 | No.
TOTAL CARRIED TO SUMMARY — WB-B EXECUTIVE STAIRCASE
SUMMARY
WB-A DOUBLE HEIGHT LOBBY
WB-B EXECUTIVE STAIRCASE
TOTAL CARRIED TO SUMMARY

## M.S Fabrication & Canopy
GOLDBOD NATIONAL ASSAY CENTER · ROOF CANOPY — FABRICATION & CLADDING BOQ
ROOF CANOPY — STRUCTURAL STEEL FABRICATION + ALUMINIUM SHEET CLADDING
ITEM | DESCRIPTION | L(m) | W/H(m) | QTY | UNIT | SQ.FT | RATE | AMOUNT
SECTION 1 — STRUCTURAL STEEL FABRICATION — CANOPY FRAME [Primary + Secondary Members]
A | Fabrication & supply — 150×75×4mm RHS primary cantilever rib frame, shop-fabricated, hot-dip galvanized | 59 |  | 171.1 | m | 561.3517
B | Fabrication & supply — 20×20mm HS secondary sheet-support grid, shop-fabricated, hot-dip galvanized |  |  | 280.2 | m | 919.2914
C | Anchor Fast fixing system — primary rib to RCC parapet/slab structure (cast-in or post-fix anchor) | 177 |  | 177 | No
D | 2" Gridwork steel stud fastener @ 16" O.C. — sheathing support fixing (per DT-01 fixing detail) | 175 |  | 175 | No
E | Full bearing high-impact resistant plastic shims — field verify as needed, at fastener points |  |  | 175 | No
F | Shop-priming + hot-dip galvanizing — all structural steel canopy members (RHS 150×75×4 + 20×20) | 2171 |  | 2171 | kg
G | Site erection, alignment, welding/bolting of fabricated steel frame to structure |  |  | 1 | LS
SUBTOTAL — STRUCTURAL STEEL FABRICATION
SECTION 2 — ALUMINIUM SHEET CLADDING — CANOPY FINISH [3mm sheet, gold-anodised, all faces]
H | 3mm aluminium sheet cladding — canopy TOP surface, gold-anodised finish, factory-formed panels | 70.04 | 2.4 | 168.1 | m² | 1809.4116
J | 3mm aluminium sheet cladding — canopy SOFFIT (curved/tapered aerofoil underside), gold-anodised | 70.04 | 2.4 | 188.27 | m² | 2026.5195
K | 3mm aluminium sheet cladding — fascia/tip edge band (900mm height), gold-anodised | 70.04 | 0.9 | 63.04 | m² | 678.5563
L | Aluminium sheet panel jointing — 'fit joint without spacer' system per manufacturer detail | 58 |  | 58 | No
M | Gridwork self-adhered weatherproofing membrane — behind cladding at face of sheathing | 419.41 |  | 419.41 | m² | 4514.4873
N | Low-modulus silicone sealant with open-cell backer rod — panel movement joints | 210 |  | 210 | Lm | 688.9764
P | 1/8" foam tape (pre-applied to bracket) — gridwork L-bracket cladding fixing points |  |  | 233 | No
Q | Indirect LED lighting strip — concealed at canopy underside root junction (per DT-01 detail) | 70.04 |  | 70.04 | Lm | 229.79
R | Weep slots @ 12" O.C. — canopy drainage at low point of soffit/fascia junction | 233 |  | 233 | No
SUBTOTAL — ALUMINIUM SHEET CLADDING
SUMMARY
ROOF CANOPY — FABRICATION & CLADDING
STRUCTURAL STEEL FABRICATION
ALUMINIUM SHEET CLADDING
ROOF CANOPY — FABRICATION & CLADDING
GRAND TOTAL — ROOF CANOPY FABRICATION & CLADDING

## Lift-BOQ
PROJECT 134 · GOLDBOD NATIONAL ASSAY CENTER · PASSENGER LIFT BOQ
PASSENGER LIFTS — EXECUTIVE LIFT & STAFF AREA LIFT (MRL TRACTION, 3 STOPS)
ITEM | DESCRIPTION | QTY | UNIT | SQ.FT/EQUIV | RATE | AMOUNT
SECTION 1 — EXECUTIVE LIFT [Shaft 2600×2100mm — Schindler 3300 MRL / Mitsubishi NEXIEZ-MRL , 13 persons]
A | MRL Gearless Traction Passenger Lift — Supply, deliver, install,
test and commission a complete Machine Room-Less (MRL) gearless
traction passenger lift of approved manufacture (Schindler 3300 MRL,
Mitsubishi NEXIEZ-MRL Version 2, or approved equivalent), with a
rated capacity of 13 persons (approximately 950–1000 kg), serving 3
stops with 3 openings, VVVF drive system, and minimum rated speed
of 1.0 m/s, complete with premium anti-fingerprint hairline stainless
steel/champagne metallic modular car interior incorporating black
mirror stainless steel accents; stainless steel or powder-coated metal
ceiling with recessed warm white LED lighting (3000–3500K), linear
LED lighting, emergency light and ventilation grille; heavy-duty
anti-slip stone, granite or large-format porcelain floor finish; minimum
100 mm high brushed or black stainless steel replaceable
kickplates/skirting; brushed hairline stainless steel handrail;
automatic centre-opening stainless steel car doors and landing doors
with matching stainless steel frames minimum 900 mm clear opening,
fire-rated where required; full-height black glass and stainless steel Car
Operating Panel (COP) complete with tactile/Braille push buttons,
digital floor position indicator, overload indicator, alarm, emergency
intercom, and provision for access control card/biometric reader
integration; landing call stations and floor position indicators to all
landings; Automatic Rescue Device (ARD/ARO), emergency lighting,
alarm bell, emergency communication system, Fireman's Operation
Switch emergency evacuation interface, CCTV camera within lift car
with provision for integration into the building security system,
temporary protective pads retained for future maintenance use,
together with all guide rails, brackets, buffers, controllers, wiring,
travelling cables, suspension system, door operators, safety devices,
fixings, accessories, builder's work coordination, statutory
inspections, performance testing, certification, warranties, operation
and maintenance manuals, user training, and all other labour,
materials, equipment and incidental works necessary to provide a
| complete operational installation. | 1 | No.
EXECUTIVE LIFT
Carried to Summary
SECTION 2 — STAFF AREA LIFT [Shaft 2300×2400mm — Schindler 13P preferred / Mitsubishi 11P alternate]
A | Supply, deliver, install, test and commission a complete Machine
Room-Less (MRL) gearless traction passenger lift of approved
manufacture (Schindler 3300 MRL preferred, or Mitsubishi
NEXIEZ-MRL Version 2 or other approved equivalent), with a rated
capacity of 13 persons or alternatively 11 persons (825 kg), serving 3
stops with 3 openings, incorporating a VVVF drive system and rated
speed of 1.0 m/s, complete with premium modular car interior
finished in anti-fingerprint hairline stainless steel and/or champagne
metallic panels with black mirror stainless steel accents; stainless
steel or powder-coated metal ceiling with recessed warm white LED
lighting (3000–3500 K), linear LED lighting, emergency lighting and
ventilation grille; anti-slip stone, granite or large -format porcelain
floor finish to match the approved interior design; minimum 100 mm
high heavy-duty replaceable brushed or black stainless steel
kickplates/skirting; brushed hairline stainless steel handrail to one
side or rear wall; automatic centre-opening car doors with matching
front return in hairline, black mirror or champagne stainless steel
finish and minimum 900 mm clear opening; full-height black glass and
stainless steel Car Operating Panel (COP) complete with tactile/Braille
push buttons, digital floor position indicator, overload indicator,
alarm, emergency intercom and provision for access card/biometric
reader integration; landing doors and frames to all three landings with
matching finish and fire rating where required; landing call stations and
digital floor indicators to all floors; Automatic Rescue Device
(ARD/ARO), emergency lighting, alarm bell, emergency
communication system, Fireman's Operation Switch and emergency
evacuation interface; CCTV camera within the lift car with provision for
integration into the building security/access control system;
temporary protective pads for use during construction and
commissioning and retained for future maintenance; together with all
guide rails, landing and car door equipment, controllers, suspension
system, travelling cables, buffers, safety gear, machine, electrical
installation, wiring, brackets, fixings, accessories, statutory
inspections, testing, commissioning, certification, operation and
maintenance manuals, warranties, user training, builder's work
coordination, and all labour, materials, plant and incidentals necessary
| to provide a complete operational lift installation. | 1 | No.
STAFF AREA LIFT
Carried to Summary
SECTION 4 — TESTING, CERTIFICATION, TRAINING & HANDOVER
A | Provide all third-party inspections, testing, commissioning,
certification and post-installation support for the complete lift
installation, including independent third-party inspection, proof load
testing, safety testing and certification for each lift in accordance with
EN 81-20, EN 81-50, or the applicable Ghanaian statutory requirements
and regulations; undertake a vertical transportation traffic analysis and
handling capacity verification upon confirmation of the final building
occupancy and population ; carry out complete commissioning,
performance testing, trial operation, Automatic Rescue Device (ARD)
operation, emergency lighting and alarm tests, emergency
communication tests, Fireman's Operation tests, safety device
verification, and all functional and acceptance tests necessary to
demonstrate full compliance with the specified performance
requirements for both lifts; provide complete as-built drawings,
operation and maintenance manuals, warranty certificates, spare parts
lists, test certificates, statutory approvals, maintenance schedules,
manufacturer's documentation, and training for the Employer's
facilities management personnel in the operation and routine
maintenance of the lift systems; and provide a comprehensive Annual
Maintenance Contract (AMC) for both lifts for the first year following
expiry of the manufacturer's warranty, including scheduled preventive
maintenance, routine inspections, emergency call-out services,
adjustments, lubrication, testing, replacement of normal wear-and-tear
components, technical support, and all labour, materials, equipment
and incidentals necessary to maintain the lifts in safe and efficient
| operating condition. |  | Item
SECTION 4 — TESTING, CERTIFICATION, TRAINING & HANDOVER
Carried to Summary
SUMMARY
EXECUTIVE LIFT
STAFF AREA LIFT
TESTING, CERTIFICATION, TRAINING & HANDOVER
PASSENGER LIFTS
Carried to General Summary

## external works
Item | Description | Qty | Unit | Rate | Amount
BILL No. 15: EXTERNAL WORKS
COMPOUND WALL
Mass in situ concrete: BS 5328, designed mix C30, 20mm
aggregate, minimum cement content 240 Kg/m3; vibrated
A | Foundations
| poured on earth | 160 | m3
Reinforced in situ concrete: BS 5328, designed mix C20, 20mm
aggregate, minimum cement content 240 Kg/m3; vibrated
B | Compound Wall, reinforced, thickness ≤ 200mm | 530 | m3
C | Ditto; Columns & Beams | 390 | m3
E20: FORMWORK FOR IN SITU CONCRETE
Wrought formwork, basic finish to
D | Sides of Compound Wall | 5701 | m2
E30: REINFORCEMENT FOR IN SITU CONCRETE
Reinforcement bars; High tensile
E | 16mm diameter in compound wall | 103.76 | t
Electric Fencing
F | Compound Wall Above Electric Fencing work_Supply,
Installation, Testing & Commissioning (SITC) of Electric
Security Fence System comprising high-tensile galvanized
steel wires mounted on heavy-duty UV-stabilized
insulators fixed over the existing exterior compound wall
using hot-dip galvanized MS/Y-shaped mounting brackets.
The work shall include energizer, battery backup, solar
power supply (if specified), lightning diverter, earthling
system, warning sign boards, tensioners, strain insulators,
gate connections alarm integration, all necessary
accessories, cabling, connectors, hardware, fixing
materials, testing, commissioning, and handing over
complete in all respects as per approved drawings,
manufacturer's specifications, and Engineer-in-Charge's
| instructions | 257 | m2
M60: PAINTING/ CLEAR FINISHING
Prepare and Apply one coat primer and two coats of emulsion
paint as described to treated wall:
General surfaces rendered concrete and
block walls
G | girth > 300mm | 1194 | m2
Prepare and Apply two coats of weatherproof exterior
paint as described to treated wall:
General surfaces rendered concrete and
block walls
E | girth > 300mm | 1194 | m2
COMPOUND WALL
Carried to Summary
TRIMIX FLOORING
Concrete Work
A | Provide and lay 100 mm thick in-situ concrete floor, Grade
25, finished with approved metallic dry-shake surface
hardener (Trimix) applied at manufacturer's
recommended rate of 3–5 kg/m², power floated to a
smooth, dense, abrasion-resistant finish, including
surface preparation, levelling, trowelling, curing, and all
| incidental labour and materials complete | 76 | m3
B | 16mm diameter high tensilel in trimix floor | 7.6 | t
TRIMIX FLOORING
Carried to Summary
GRANITE FLOORING
C | Supply and fix 20 mm thick polished natural granite floor
tiles, approved colour and pattern, bedded and jointed in
20 mm thick cement and sand (1:3) mortar, joints pointed
with matching coloured cement grout, including cutting,
| fitting, trimming, waste. | 380 | m2
GRANITE FLOORING
Carried to Summary
SURVELLIANCE ROOM
Mass in situ concrete: BS 5328, designed mix C30, 20mm
aggregate, minimum cement content 240 Kg/m3; vibrated
A | Foundations
| poured on earth | 19 | m3
Reinforced in situ concrete: BS 5328, designed mix C20, 20mm
aggregate, minimum cement content 240 Kg/m3; vibrated
B | Slabs reinforced, thickness ≤ 150mm | 22 | m3
C | Beams, reinforced | 9 | m3
D | Columns reinforced | 6 | m3
E20: FORMWORK FOR IN SITU CONCRETE
Wrought formwork, basic finish to
E | Slabs | 125 | m2
F | Beams | 82 | m2
G | Columns | 41 | m2
H | Shear Walls | 186 | m2
E30: REINFORCEMENT FOR IN SITU CONCRETE
Reinforcement bars; High Tensile
E | 16mm diameter in Slab, Beam & Column | 8.76 | t
J31 LIQUID APPLIED WATERPROOF ROOF COATINGS
Provide and applying cementitius crystalyn waterproofing
treatment by brush/spray application in 2 coats on RCC
slabs, walls, water tanks, lift pit, Etc. as per manufecturer's
specification.
A | Roof
| width > 300mm | 125 | m2
C/F
B/F
K: LININGS/ SHEATHING/ DRY
PARTITIONING
A | Providing and fixing suspended gypsum board false ceiling
using 12.5mm thick tapered edge gypsum plaster board
conforming to IS:2095, including G.I. perimeter channel of
0.5mm thick having 20mm x 27mm x 30mm, G.I.
intermediate channel 0.9mm thick 15mm x 45mm x 15mm
@ 1220mm c/c, and G.I. ceiling section 0.5mm thick
51.5mm x 26mm @ 457mm c/c, suspended from soffit
| with G.I. hanger @ 1220mm c/c. Complete as per drawing | 120 | m2
L: WINDOWS/ DOORS/ STAIRS
L20: DOORS/SHUTTERS/HATCHES
DOORS
Wrought Walnut hardwood with trim moulding or approved equal in two panels as described
B | Hardwood framed single-leaf Solid Core panel door 1200
| x2450x50mm (Finished), | 1 | Nr
M: SURFACE FINISHES
M10: CEMENT: SAND/ CONCRETE SCREEDS/
TOPPINGS
Screed, cement and sand (1:4) trowelled smooth
C | Floors
| 50mm thick, level and to falls only ≤ 150 | 125 | m2
M20: PLASTERED/ RENDERED/
ROUGHCAST COATINGS
Wall Punning
D | Provide and apply 2 coats wall punning 8-12mm with
chicken mesh, using approved quality wall putty /
cement-based punning material over prepared wall
surfaces, including cleaning, surface preparation, curing,
and finishing smooth and even, complete in all respects as
| per specifications | 260 | m2
Porcelain Italian marble tiles 600 x 600 x 10mm thick approved colour,two symmetrical joints layout, bedding in an approved adhesive; pointing with approved matching colour tile grout with on cement sand backing
E | Floor
| plain, width > 300mm | 125 | m2
C/F
B/F
M60: PAINTING/ CLEAR FINISHING
Prepare and Apply one coat primer and two coats of emulsion
paint as described to treated wall:
General surfaces rendered concrete and
block walls
A | girth > 300mm | 125 | m2
SURVELLIANCE ROOM
Carried to Summary
UNDERGROUND WATER TANK
B | Providing and constructing a Reinforced Cement Concrete (R.C.C.) underground water tank complete as per approved drawings and specifications, including excavation, dewatering (if required), PCC, RCC base slab, walls and top slab with reinforcement, centering & shuttering, waterproofing admixture, PVC water stops at construction joints, internal and external waterproof plaster, curing, backfilling and compaction. The item shall also include all necessary sleeves, puddle flanges, inlet, outlet, overflow and drain connections, manholes with covers, access ladder, vent pipe, water-tightness testing, disposal of surplus excavated material, and all labour, materials, machinery, tools & tackles, transportation, and incidental works required for complete execution and commissioning of the tank. | 1 | No.
UNDERGROUND WATER TANK
Carried to Summary
BILL No. 15: EXTERNAL WORKS
SUMMARY
COMPOUND WALL
TRIMIX FLOORING
GRANITE FLOORING
SURVELLIANCE ROOM
UNDERGROUND WATER TANK
BILL No. 15: EXTERNAL WORKS
CARRIED TO GENERAL SUMMARY

## Summary
Item | Description | Qty | Unit | Rate | Amount
GENERAL SUMMARY
BILL No. 1: PRELIMINARIES AND GENERAL ITEMS
BILL No. 2: SUBSTRUCTURE
BILL No. 3 - GROUND FLOOR
BILL No. 4 - FIRST FLOOR
BILL No. 4 - SECOND FLOOR
BILL No. 5 - ELECTRICAL WORK
BILL No. 6 - HVAC WORK
BILL No. 7 - PLUMBING WORKS
BILL No. 8 - FIRE INSTALLATIONS
BILL No. 9 - FURNITURE
BILL No. 10- SECURITY INSTALLATIONS (VEHICLE ACCESS CONTROL)
BILL No. 11 - SECURITY INSTALLATIONS (SECURITY SYSTEM INTEGRATION)
BILL No. 12- WATER BODIES
BILL No. 13- ROOF CANOPY
BILL No. 14 - LIFT
BILL No. 15: EXTERNAL WORKS
SUB-TOTAL
Add:
Provisional sum for Physical contingencies (5%)
Provisional sum for Price contingencies (5%)
TOTAL CARRIED TO TENDER FORM